## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: WAPCOS Limited
Work Name : Construction of W&C Block at DH Nilambur - Electrical
Contract No: WAP/INFRA/KERALA/25/NLBR/504-3
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Electrical Works | BI01010001010000000000000515BI0100001113 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | 1.10.3 : Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.Group C |  | 570 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 1.14.1 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required2x1.5 sq.mm + 1x1.5 sq.mm earth wire |  | 1200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | 1.31 : Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). |  | 72 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.04 | 1.24.1 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.5/6 amps switch |  | 12 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.05 | 1.24.3 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.15/16 amp switch |  | 325 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.06 | 1.24.4 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.3 pin 5/6 amp socket outlet |  | 18 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | 1.24.5 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.6 pin 15/16 amp socket outlet |  | 325 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.08 | 1.25 : Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. |  | 103 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.09 | 1.27.1 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.1 or 2 Module (75mmX75mm) |  | 92 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.1 | 1.27.2 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.3 Module (100mmX75mm) |  | 59 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | 1.27.3 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.4 Module (125mmX75mm) |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | 1.27.4 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.6 Module (200mmX75mm) |  | 129 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | 1.27.5 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.8 Module (125mmX125mm) |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | 1.33 : Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | 1.47 : Supplying and fixing extra down rod of 10 cm length G.I. pipe, 15 mm dia, heavy gauge including painting etc. as required. (Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) |  | 60 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | 1.58 : Supplying and fixing PVC batten/ angle holder including connection etc. as required. |  | 52 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | 90.3.19.3 : Supply conveyance, installation, testing and commissioning the light fittings of following types made from CRCA sheet 0.5mm thickness with all accessories and lamps directly on wall and giving connections with 16/0.20 mm 3 core PVC insulated and sheathed round copper conductor flex wire or extending the original wiring and giving connections as required |  | 223 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | 90.3.20.3 : Supply & installation of light fittings on TW round block <br> Supply, conveyance installation testing and commissioning the light fittings of following types made of CRCA with 0.5mm thickness complete with all accessories and lamps etc. directly on wall or ceiling with PVC round block neatly painted to suit the fitting and giving connection with required length of 16/0.20mm 3 core copper conductor flex wire conforming to relevant ISS and giving connections as required. |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | od243495/2023_2024 : Supplying and fixing following rating, double pole, 240 volts, MCB type center OFF COS in the existing MCB DB complete with connections, testing and commissioning etc. as required.&lt;br&gt;40 amps |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | od243496/2023_2024 : Supply, conveyance, installation , testing and commissioning of 300/305 mm sweep Light Duty Exhaust fan in metal frame working on 230 V A/C in the existing opening, fixing necessary anchor bolts / bolt and nuts etc., as required including giving connections with the supplied wire along with the exhaust fan. |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | od243497/2023_2024 : Supply, conveyance, installation , testing and commissioning of 250 mm sweep Light Duty Exhaust fan in plastic body with self opening lowers working on 230V single phase A/C , fixing necessary anchor bolts / bolt and nuts etc., as required including giving connections with the supplied wire along with the exhaust fan. |  | 44 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | od243498/2023_2024 : Supply and fixing syntex make SMC junction box with hinged door having inside dimensions 200x140x95mm for terminal box fixing on wall using suitable screws and plugs etc as required for test joint junction (Syntex make GSJB2014) |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | od243499/2023_2024 : Supplying and fixing 9W LED Bulb. as required.&lt;br&gt; |  | 68 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | od243500/2023_2024 : Supply, conveyance, installation, testing and commissioning of Bulk head light fittings directly on wall including giving connections with required length of 16/0.20mm 3 core round copper conductor flex wire conforming to relevant ISS making good the damages, colour washing etc as required. |  | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | od243501/2023_2024 : Supplying and fixing 200mm Plastic sill shade. as required. |  | 52 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | od243502/2023_2024 : Supply conveyance and fixing of down light fittings 3600 lumen square (2ft X 2ft) recessed fitting made of crca sheet of thickness 0.5mm, having efficacy not less than 110l/w, pf greater than 0.95, THD less than or equal to 10%, Chip make Cree/Osram/lumilled/Nichea of complete with all accessories in the cutting of false ceiling, giving connections with the existing wire etc., as required. |  | 24 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | od243503/2023_2024 : Supply, conveyance, installation, testing and commissioning of 1200 lumen round/ square surface mount fitting made of diecast aluminium, having efficacy not less than 100l/w, pf greater than 0.95, THD less than or equal to 10%, Chip make Cree/Osram/lumilled/Nicheaall types directly on ceiling including giving connections with required length of 16/0.20 mm 3 core round copper conductor flex wire conforming to relevant ISS or with the extended original wiring, making good the damages, colour washing etc as required. |  | 18 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | 90.3.24.3 : Supply & installation of light fittings suspended on ball & socket arrangement with 19 mm down rod <br> Supply, conveyance, installation, testing and commissioning the light fittings of following types made of .5mm thick CRCA sheet accessories and lamps etc. including supplying and fixing ball and socket arrangements on PVC round block, suspension down rod of 19mm dia MS conduit up to 2x30cm length including painting and wiring the down rod with 16/0.20mm 3 core round copper conductor flex wire conforming to relevant ISS or extending the original wiring and giving connections etc. a required. |  | 67 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | 90.4.1 : Supply and installation of suitable size MS rod type fan clamp in the RCC slab as per IS 732 as required. |  | 103 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | 90.5.1.3 : Supply and fixing the following types of superior quality 250V A.C call bell on existing M.S. box and giving connections with required length of 3 core, 16 / 0.20mm 650/1100V grade PVC insulated and PVC sheathed round copper conductor flex wire conforming to relevant ISS or with the extended original wiring, earthing the MS box and making good the surface as required. |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | 90.5.1.4 : Supply and fixing the following types of superior quality 250V A.C call bell on existing M.S. box and giving connections with required length of 3 core, 16 / 0.20mm 650/1100V grade PVC insulated and PVC sheathed round copper conductor flex wire conforming to relevant ISS or with the extended original wiring, earthing the MS box and making good the surface as required. |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | 90.15.4.7 : Supply Conveyance, installation, testing and commissioning of 100W LED Flood light output greater than 105lumen/W 4000-6000 K with IP 66 protection LED Chip make Cree/Lumilled/Nichea with power factor greater than 0.95 at full load, internal surge protection up to 8 KV,and Aluminium pressure die-cast Powder coated housing, acrylic cover complete with THD less than 10%, power factor greater than 0.98, RoHS compliant, duly wired up for use on 230 V AC supply. Driver compartment should be seperatly accessible for maintenance (LM 79&80 certificates from NABL accredited Third party lab to be produced mentioning chip manufacturer) |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | od43698/2024_2025 : Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374- 2019), THD less than 10%, remote or electronics regulator for speed control and all remaining accessories including safety pin, nut bolts, washers,temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. |  | 103 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | 90.4.8 : Charges for cutting holes suitable for accommodating exhaust fans up to 305mm sweep including plastering colour washing etc. as required. |  | 49 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | 90.10.3.15 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 57 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.36 | 90.10.3.33 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 44 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.37 | 2.3.2 : Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCBIRCCB/Isolator8 way, Double door |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.38 | 2.3.3 : Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCBIRCCB/Isolator12 way, Double door |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.39 | 90.11.1.11 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.4 | 90.11.1.14 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.41 | 90.11.1.15 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.42 | 90.11.1.16 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.43 | 2.10.1 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Single pole |  | 428 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.44 | 2.10.4 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Triple pole |  | 28 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.45 | 2.10.5 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Triple pole and neutral |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.46 | 2.11 : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. |  | 127 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.47 | 2.12.1 : Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.48 | 2.13.1 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.49 | 2.13.2 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.63 amps |  | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.5 | 2.14.2 : Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.51 | 2.15.2 : Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 17 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.52 | 2.15.3 : Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.63 amps |  | 13 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.53 | 90.10.3.23 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.54 | 90.9.1.1 : Supply and fixing 50 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.55 | 90.9.1.7 : Supply and fixing 50 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.56 | 90.9.2.1 : Supply and fixing 100 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.57 | 90.9.2.8 : Supply and fixing 100 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.58 | 90.9.2.12 : Supply and fixing 100 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.59 | 90.9.2.14 : Supply and fixing 100 x 50 mm PVC Cable Management System with base and lid along with the following accessories conforming to IEC 61084/ BS 476 & 4678 on surface / recess including cutting the wall and making good the damages in case of recessed installation as required. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.6 | 1.17.3 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 X 1.5 sq.mm |  | 150 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.61 | 1.17.6 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.6 x 1.5 sq. mm |  | 250 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.62 | 1.17.9 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.9 x 1.5 sq. mm |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.63 | 1.17.15 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.6 x 2.5 sq. mm |  | 500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.64 | 1.17.18 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.9 x 2.5 sq. mm |  | 300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.65 | 1.17.24 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.6 x 4 sq. mm |  | 100 | mm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.66 | 1.17.7 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.7 x 1.5 sq. mm |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.67 | 1.17.12 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 2.5 sq. mm |  | 100 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.68 | 1.17.14 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.5 x 2.5 sq. mm |  | 500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.69 | 1.17.16 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.7 x 2.5 sq. mm |  | 300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.7 | 1.17.21 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 4 sq. mm |  | 500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.71 | 1.17.23 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.5 x 4 sq. mm |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.72 | 1.17.30 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 6 sq. mm |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.73 | 1.21.1 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm |  | 2500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.74 | 1.21.2 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.25 mm |  | 570 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.75 | 1.28.2 : Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.3 Module |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.76 | 1.28.5 : Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.8 Module |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.77 | 90.12.5.31 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.78 | 90.12.5.32 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.79 | 90.12.5.34 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.8 | 90.12.7.3 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 250 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.81 | 90.12.7.30 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 175 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.82 | 90.12.7.31 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.83 | 90.12.7.32 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.84 | 90.12.7.34 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 35 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.85 | 90.12.7.40 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 400 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.86 | 90.12.7.41 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 100 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.87 | 90.12.7.42 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.88 | 9.1.2 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.2 X 10 sq. mm (19mm) |  | 16 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.89 | 9.1.23 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 70 sq. mm (38mm) |  | 12 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.9 | 9.1.24 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 95 sq. mm (45mm) |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.91 | 9.1.25 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2 X 120 sq. mm (45mm) |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.92 | 9.1.27 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 185 sq. mm (57mm) |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.93 | 9.1.32 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 10 sq. mm (25mm) |  | 24 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.94 | 9.1.33 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 16 sq. mm (28mm) |  | 10 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.95 | 9.1.34 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 25 sq. mm (28mm) |  | 40 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.96 | 90.12.9.4 : Supplying, laying and jointing of the following sizes of double wall corrugated (DWC) pipes made out of HDPE conforming to IS 14930 Part II for mechanical protection to underground power cables with all required accessories in ground in the existing trench |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.97 | 90.12.9.6 : Supplying, laying and jointing of the following sizes of double wall corrugated (DWC) pipes made out of HDPE conforming to IS 14930 Part II for mechanical protection to underground power cables with all required accessories in ground in the existing trench |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.98 | 90.12.9.7 : Supplying, laying and jointing of the following sizes of double wall corrugated (DWC) pipes made out of HDPE conforming to IS 14930 Part II for mechanical protection to underground power cables with all required accessories in ground in the existing trench |  | 35 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.99 | 90.14.5 : Supply and fabrication conveyance and installation of angle iron frame work for wall mounting panel board |  | 410 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | 4.1.4 : Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.300 mm width X 50 mm depth X 1.6 mm thickness |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.01 | 4.1.6 : Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.450 mm width X50 mm depth X 2.0 mm thickness |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.02 | 5.4 : Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | 90.14.1.2 : Fabrication, supply, conveyance, installation testing and commissioning of floor or wall mounting, dust and vermin proof, cubicle type MV panel board comprising of the following components/ devices & complying to IS 8623.<br> Fabrication of fully partitioned, dust and vermin proof enclosure for panel assembly as per form 4 of IS 8623 (with latest amendments) using CRCA sheet as per approved design and requirement, with front and rear access facility, bus bar chambers, hinged doors for all switch gear compartments, earthing the doors using 4 sq mm braided copper conductor, providing necessary cut-outs for mounting meters, relays, indication lamps, bus bar interconnection etc, detachable covers for bus bar chamber and cable alley, powder coating the assembly after subjecting to 7 tank process etc as required. CRCA sheet alone be used for the fabrication. Angles/ flats/ slotted angles etc shall not be used for the fabrication of panel assembly. The measurments will be taken the area of the complete sheets used for panel board including partitions, folding, shrouding etc. |  | 79 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | 90.14.2.1 : Supply and providing 2mm SMC sheet as shrouding for bus interconnection / terminations etc. including required nut & bolt etc. |  | 11 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.05 | 90.14.3.1 : Supply and providing heavy duty 'A' section neoprene gasket in the panel board |  | 154 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.06 | 90.14.4 : Supply and fabrication conveyance and installation of base frame of panel board using 75 x 40 mm rolled steel channel (ISMC) |  | 4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.07 | 90.14.6 : Supply and providing copper bus bars including finger type SMC bus bar supports in the bus chamber, suitable size nut & bolt, providng heat shrink sleeves etc. as required. |  | 18130 | Cum cm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.08 | 90.14.7 : Supply and providing copper earth bus in the panel board |  | 2700 | Cum cm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.09 | 90.14.10.4 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 35 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.1 | 90.14.10.11 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 14 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.11 | 90.14.10.14 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.12 | 90.14.10.15 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.13 | 90.14.11.12 : MCCB Accessories |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.14 | 90.14.11.13 : MCCB Accessories |  | 49 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.15 | 90.14.11.15 : MCCB Accessories |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.16 | 90.16.1.2 : Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required |  | 1300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.17 | 90.16.1.3 : Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required |  | 1000 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.18 | 90.16.1.4 : Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required |  | 600 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.19 | 90.16.3.9 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.2 | 90.16.3.10 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.21 | 90.16.3.11 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.22 | 90.16.3.12 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run)32 x 6 mm copper strip |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.23 | 90.16.4.11 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run).32 x 6 mm copper strip |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.24 | 90.16.4.8 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 60 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.25 | 90.16.4.9 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.26 | 90.16.4.10 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.27 | od244848/2023_2024 : Supply and fixing 200A,415V,4pole 50Hz Auto Transfer Switch with controller and control&lt;br&gt;contractor if required in the existing panel board and giving connection etc as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.28 | od244849/2023_2024 : Supply and fixing the 400A 415V 4Pole 50Hz Auto Transfer switch with controller and&lt;br&gt;connected control contractor if required and connector wire with plugs in existing panel board&lt;br&gt;including giving connection etc as required. ATS should be operate for DG auto start/stop&lt;br&gt;function (L&amp;amp;T make or equalent)&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.29 | od244850/2023_2024 : Supply and providing 12x3mm brass bolt |  | 100 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.3 | od244851/2023_2024 : Supply and providing 25x3mm brass bolt |  | 100 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.31 | od244852/2023_2024 : Supply and providing 25x6mm brass bolt |  | 100 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.32 | 90.16.5.2 : Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required. |  | 60 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.33 | 90.16.5.3 : Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required. |  | 50 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.34 | 90.16.5.4 : Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required. |  | 30 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.35 | 2.1.5 : Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.160 Amp TP&N |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.36 | od244903/2023_2024 : Supply and wiring with PVC insulated stranded single core copper conductor cables for&lt;br&gt;interconnecting the control devices/ equipment&apos;s including the wiring firm by suitable tie/ tie&lt;br&gt;mounts/ PVC duct etc as required. 1.5Sqmm single run |  | 280 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.37 | od244904/2023_2024 : Supply and wiring with PVC insulated stranded single core copper conductor cables for&lt;br&gt;interconnecting the control devices/ equipment&amp;#39;s including the wiring firm by suitable tie/&lt;br&gt;tie mounts/ PVC duct etc as required. 6Sqmm single run |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.38 | od244905/2023_2024 : Supply and wiring with PVC insulated stranded single core copper conductor cables for&lt;br&gt;interconnecting the control devices/ equipment&amp;#39;s including the wiring firm by suitable tie/&lt;br&gt;tie mounts/ PVC duct etc as required. 10Sqmm single run |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.39 | od244906/2023_2024 : Supply and fixing 230V,50Hz Cooling fan in the existing panel board and giving connection&lt;br&gt;etc. as requireD |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.4 | od244907/2023_2024 : Supplying and fixing 24Hr Analog Timer switch with NO/NC operating voltage 230V in the&lt;br&gt;existing MCB DB complete with connections, testing and commissioning etc. as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.41 | od244908/2023_2024 : Supply and fixing 8 stage 440 / 110 V 5A/1A , Intelligent Power Factor Controllers (IPFC) in&lt;br&gt;existing panel board and giving connection etc as required. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.42 | od244909/2023_2024 : Supply and fixing push button NO/NC in the existing panel board and giving connection etc. as&lt;br&gt;required |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.43 | od244910/2023_2024 : Supply and fixing Auto/Manual Selector Switch in existing Panel and giving connection etc. as&lt;br&gt;required (8pole 2way) |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.44 | od244911/2023_2024 : Supply and fixing 3 Pole Capacitor duty contactors for switching capacitor banks 4 - 7 kVAR&lt;br&gt;with AC Coil, including suitable no NO/NC auxiliary contractor in existing panel board and&lt;br&gt;giving connection etc as required |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.45 | od244912/2023_2024 : Supply and fixing 3 Pole Capacitor duty contactors for switching capacitor banks 7.5-10 kVAR&lt;br&gt;with AC Coil, including suitable no NO/NC auxiliary contractor in existing panel board and&lt;br&gt;giving connection etc as required.&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.46 | od244913/2023_2024 : Supply and fixing 3 Pole Capacitor duty contactors for switching capacitor banks 11-15 kVAR&lt;br&gt;with AC Coil, including suitable no NO/NC auxiliary contractor in existing panel board and&lt;br&gt;giving connection etc as required. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.47 | od244914/2023_2024 : Supply and fixing 100/5A Cast resin Metering CT including connection in existing Panel board |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.48 | od244915/2023_2024 : Supply and fixing 150/5A Cast resin Metering CT including connection in existing Panel board |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.49 | od244916/2023_2024 : Supply and fixing 200/5A Cast resin Metering CT including connection in existing Panel board |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.5 | od244917/2023_2024 : Supply and fixing 250/5A Cast resin Metering CT including connection in existing Panel board |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.51 | od244918/2023_2024 : Supply and fixing Multifunction meter to read: V, A, F, 3 phase accuracy class 1 in existing Panel board including giving connection etc as required |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.52 | od244919/2023_2024 : Supply and fixing Multifunction meter to read:W, Wh, PF or VA, Vah, PF or VAR, VARh, PF,&lt;br&gt;3 ph accuracy class 1 in existing Panel board including giving connection etc as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.53 | od244920/2023_2024 : Supply and fixing LED indication lamp for all voltage ranges- Red, Green, Blue, Yellow,&lt;br&gt;colour in existing panel and giving connection etc as required |  | 32 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.54 | 90.14.24.31 : Supply & fixing the following Power Capacitors 3 phase delta connected in positon and giving connection. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.55 | 90.14.24.34 : Supply & fixing the following Power Capacitors 3 phase delta connected in positon and giving connection. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.56 | 90.14.24.36 : Supply & fixing the following Power Capacitors 3 phase delta connected in positon and giving connection. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.57 | 2.21 : Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.58 | od246442/2023_2024 : Supply and providing 9 Litre capacity GI Fire Bucket painted in post office red with primer coat&lt;br&gt;of red oxide and written with white paint &apos;FIRE&apos; mounted on MS angle frame work/ wall bracket&lt;br&gt;filled with fine sand, painting the bracket/ floor stand including making good the damages, colour washing etc. as required |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.59 | od246443/2023_2024 : Supply and providing 5 Kg. Automatic Modular ABC Powder Type Fire Extinguisher and&lt;br&gt;clamps/supports including fixing it to ceiling as required. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.6 | od179388/2024_2025 : Supply and providing 4/5 Kg. Dry Chemical Powder type Fire Extinguisher with&lt;br&gt;hose and&lt;br&gt;clamps including fixing it to wall as required. |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.61 | od246445/2023_2024 : Supply and providing 2.5mm thick synthetic VC fire retardent insulating sheet to withstand 3.3&lt;br&gt;KV dielectric strength conforming to IS |  | 10 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.62 | od246446/2023_2024 : Supply and providing First Aid Chart duly framed and placed in a conspicuous location for&lt;br&gt;clear vision. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.63 | od246447/2023_2024 : Painting letters or figures with enamel paint as identification mark to SB, DB, panel board etc as required |  | 750 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.64 | od44044/2024_2025 : Supply and providing 2.5/3mm tick and 1m wide electrical grade chequired type elastomeric mat to withstand 3.3 kV dielectric strength conforming to IS 15652:2006 |  | 10 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.65 | od246448/2023_2024 : Supply and fixing Emergency push button with enclosure of MS Construction in surface/recess&lt;br&gt;with stainless steel chain &amp;amp; hammer assembly Complete with glass and push button on&lt;br&gt;wall and giving connection etc. as required |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | DG SET | [7 empty] | 1
3.01 | 14.10 : Providing and laying in position reinforced cement concrete 1 :2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc. including form work etc. as required (excluding reinforcement). |  | 6 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.02 | od179527/2024_2025 : Supply installation and commissioning of 160 kVA Diesel Generator set complete&lt;br&gt;with integral acoustic enclosure as per existing CPCB IV norms and as per technical details given below 1. b) Type of Engine - Diesel Engine c) No. of Cylinders- As per std. d) Method of Cooling;&lt;br&gt;Liquid cooled with radiator. e) Aspiration -Turbo charged, charge after cooled. f)&lt;br&gt;Design Suitable for generating set operating. g) Output- As per manufactures&lt;br&gt;standards. 2. Standard accessories with Diesel Engine. a) Fly wheel to suit&lt;br&gt;flexible coupling b) Close Coupling c) Air cleaner d) Radiator with fan provided&lt;br&gt;with fan guard. e) Fuel Pump f) Electronic Governor g) Fuel filter h) Exhaust&lt;br&gt;silencer i) Exhaust Muffler j) Lubricating oil filter. k) Battery Charger/Generator 3.&lt;br&gt;Engine Instrument Panel with the following items a) Starting switch with key or&lt;br&gt;button/Auto manual operation b) Lubricating oil pressure gauge. c) Water&lt;br&gt;temperature gauge. d) RPM Indicator with hour meter. e) Battery charging&lt;br&gt;Ammeter. 4. Safety Controls for Engine. a) Trip for low lubricating oil pressure. b)&lt;br&gt;Trip for high water temperature. 5.Fuel pipe: Oil resistance flexible hoses of 20mm dia or nearest size MS pipe as per manufacturers standard, 6 Brush less&lt;br&gt;Alternator b) Type Self exited and selfregulated, brush less c) Capacity; 160kVA/ 128 K W @ 0.8PF d)&lt;br&gt; System of Voltage - 3 phase, 415 V, 4 wire system. e) Speed - 1500 rpm f) Voltage&lt;br&gt; regulation band - +/-2.5% of rated voltage g) Frequency - 50 Hz h) Insulation - Class-F/H .The Alternator should confirm to IS Operation and service manual shall be&lt;br&gt; provided.7.Fuel Tank Suitable size built in type integrated with the&lt;br&gt;acoustic&lt;br&gt; enclosure. Fuel connection shall be done as per standards.7.&lt;br&gt;Battery. Suitable size&lt;br&gt; built in type integrated battery with leads and terminals&lt;br&gt;of appropriate AH capacity as&lt;br&gt; per Manufactures requirement. 8.Supply of&lt;br&gt;75% HSD of fuel tank capacity for test&lt;br&gt; and trail run, 9. The standard Electric&lt;br&gt;control panel integrated with acoustic enclosure&lt;br&gt; comprising of the following.&lt;br&gt;a) 250A,4Pole MCCB set at 220A with stand by low set&lt;br&gt; earth fault relay using NCT b) Digital Multi function meter with accuracy class 1 to&lt;br&gt; read parameters such as KW, KVA, PF, voltage, Current Frequency etc: c) Digital&lt;br&gt; type single function KWH meter with accuracy class 1, d) external source power&lt;br&gt; (230V AC) battery charger e) Provision for connecting Auto start (AMF/ATS&lt;br&gt; connection),10.Exhaust Piping, Exhaust Piping shall be vent to the top of the nearest&lt;br&gt; tallest building if required . If the pipe cannot be clamped/fixed to the building or any&lt;br&gt; other structure of permanent nature necessary fabricated structures using channel&lt;br&gt; section or angle iron sections of adequate mechanical strength, duly painted with 2&lt;br&gt; coats of Heat retardant aluminum paint shall be provided for the support of the&lt;br&gt; exhaust pipe. (Additional piping will be measured excluding the standard length of&lt;br&gt; pipe supplied by the manufacturer.) including arranging load test at site or company&lt;br&gt; assembly unit- 3 Year Warranty |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.03 | 90.14.5 : Supply and fabrication conveyance and installation of angle iron frame work for wall mounting panel board |  | 410 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.04 | 90.12.5.34 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 35 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.05 | 90.12.9.7 : Supplying, laying and jointing of the following sizes of double wall corrugated (DWC) pipes made out of HDPE conforming to IS 14930 Part II for mechanical protection to underground power cables with all required accessories in ground in the existing trench |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.06 | 1.21.1 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm |  | 2500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.07 | 90.6.5.11 : Supply and drawing the following sizes of multi-core PVC insulated & FRLS PVC sheathed 650/1100 V grade copper conductor round flexible cables conforming to IS 694 part I 1960 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.08 | 90.6.5.12 : Supply and drawing the following sizes of multi-core PVC insulated & FRLS PVC sheathed 650/1100 V grade copper conductor round flexible cables conforming to IS 694 part I 1960 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.09 | 90.16.4.8 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.1 | 5.4 : Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 3 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.11 | od244851/2023_2024 : Supply and providing 25x3mm brass bolt |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.12 | od244852/2023_2024 : Supply and providing 25x6mm brass bolt |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4 | USS &amp; HT SYSTEM | [7 empty] | 1
4.01 | 14.10 : Providing and laying in position reinforced cement concrete 1 :2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc. including form work etc. as required (excluding reinforcement). |  | 5 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.02 | od179243/2024_2025 : Supply, conveyance, installation, testing and commissioning of 200K.V.A unitized sub station&lt;br&gt;comprising of H.T. panel trunked with cast resin Transformer with load break switch/ Air break&lt;br&gt;switch and manually operated on H.T. side, with top/bottom entry cable box, 315A, 4 pole&lt;br&gt;50kA M.C.C.B on L.T. side as per technical details furnished below. 1. H.T. Portion consists of&lt;br&gt;(1) 1 No 11K.V, 630A, 350M.V.A Air break/Load break switch suitable for 3 phase,3wire,50&lt;br&gt;Hz system with suitable H.R.C. fuses of appropriate rating with earth inter lock with main&lt;br&gt;switch and mechanical ON/OFF indication,(2)shunt trip coil for the remote operation of the the&lt;br&gt;load break switch, 2. Supply of 200 K.V.A , 11 K.V/433V, 50 Hz, Delta/Star connected cast&lt;br&gt;resin insulated copper wound transformer. The core shall be made of high grade grain oriented&lt;br&gt;silicon M4 steel lamination insulated and oxide layer and outside of the core shall be protected&lt;br&gt;against corrossion by epoxy resin finish.Class &amp;#39;F&amp;#39; insulation level shall be&lt;br&gt;maintained. OFF load tap changing facility shall be incorporated so as to achive tap position of&lt;br&gt;2.5% x 4 The transformer shall confirm to IEC 726 and IS 11171/1985 reaffirmed in IS2026/&lt;br&gt;1991. 3. The LT portion shall be provided with 1No 4Pole 315A 50KA isolation duty type&lt;br&gt;MCCB with with microprocessor based release with overload setting of 50 - 100% with inbuilt&lt;br&gt;earth fault relay and All inter connection from HT load break switch to transformer and to LT&lt;br&gt;breaker shall be given using electrolytic copper bus bar insulated with heat shrink sleeves and&lt;br&gt;tinned at the point of contacts. including suitable size NCT, MC12 relay, shunt trip coil in&lt;br&gt;exting MCCB for additional earth fault protection, All internal earth connections are to be given&lt;br&gt;as per standards. Necessary protection shall be made for giving cable connections on the HT&lt;br&gt;side as well as LT side. Phase barriers and shrouding as per rules has to be given. The&lt;br&gt;enclousure shall comply to IP 20 stanards and shall be powder coated over after seven tank&lt;br&gt;processing and phosphating. The USS shall be installed as per the directions at site |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.03 | od249005/2023_2024 : Supply and laying of 1no: PVC insulated and PVC sheathed armoured aluminum power&lt;br&gt;cable,11KV grade of the following sizes in the existing RCC/HUME/STONE WARE/GI/DWC&lt;br&gt;pipe as required. 3 core 300 sqm stranded compact circular aluminium conductor,conductors&lt;br&gt;screened with extruded semi conducting compound XLPEinsulated , insulation screened with&lt;br&gt;extruded semi conducting compound in combination with copper tape(0.3 KA for 1 sec.) cores&lt;br&gt;laid up. inner sheath of PVC tape,galvanized steel flat strip armoured, and overall PVC sheathed&lt;br&gt;cable conforming to IS:7098 part II 1985 with latest amendments&lt;br&gt; |  | 120 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.04 | od249006/2023_2024 : Supply, laying of 1no: PVC insulated and PVC sheathed armoured aluminium power&lt;br&gt;cable,11KV grade of the following sizes in the existing masopnry open duct as required. 3 core&lt;br&gt;300 sqm stranded compact circular aluminium conductor,conductors screened with extruded&lt;br&gt;semi conducting compound XLPEinsulated , insulation screened with extruded semi conducting&lt;br&gt;compound in combination with copper tape(0.3 KA for 1 sec.) cores laid up.inner sheath of&lt;br&gt;PVC tape,galvanized steel flat strip armoured, and overall PVC sheathed cable conforming to&lt;br&gt;IS:7098 part II 1985 with latest amendments |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.05 | od249007/2023_2024 : Supply, conveyance, installation, testing and commissioning of Out Door type CT PT unit PT&lt;br&gt;11KV/110V 100VA CL0.2 CT 3Nos ---/5A 15VA CL0.2 (Ratio suggested by KSEB) and&lt;br&gt;fixing in the existing KSEB DP Structure after removing the existing CT and giving connection&lt;br&gt;including arranging testing the CT from TMR and arranging technical staff for TMR for&lt;br&gt;charging time. The CTPT shall be installed as per the directions at site. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.06 | od249008/2023_2024 : Supply, conveyance, installation, testing and commissioning of H.T. Multi panel one incoming&lt;br&gt;and 2Nos outgoing trunked with top/bottom entry cable box, Panel Portion consists of (1) 3Nos&lt;br&gt;11K.V, 630A, 350M.V.A Air break/Load break switch suitable for 3 phase,3wire,50 Hz system&lt;br&gt;with suitable H.R.C. fuses of appropriate rating with earth inter lock with main switch and&lt;br&gt;mechanical ON/OFF indication,(2)shunt trip coil for the remote operation of the the load break&lt;br&gt;switch, All inter connection to HT load break switch shall be given using electrolytic copper&lt;br&gt;bus bar insulated with heat shrink sleeves and tinned at the point of contacts. All internal earth&lt;br&gt;connections are to be given as per standards. Necessary protection shall be made for giving&lt;br&gt;cable connections on the HT side Phase barriers and shrouding as per rules has to be given. The&lt;br&gt;enclousure shall comply to IP 20 stanards and shall be powder coated over after seven tank&lt;br&gt;processing and phosphating. The Panel shall be installed as per the directions at site. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.07 | 90.14.5 : Supply and fabrication conveyance and installation of angle iron frame work for wall mounting panel board |  | 50 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.08 | 90.6.5.11 : Supply and drawing the following sizes of multi-core PVC insulated & FRLS PVC sheathed 650/1100 V grade copper conductor round flexible cables conforming to IS 694 part I 1960 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.09 | 90.6.5.12 : Supply and drawing the following sizes of multi-core PVC insulated & FRLS PVC sheathed 650/1100 V grade copper conductor round flexible cables conforming to IS 694 part I 1960 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.1 | 90.12.9.8 : Supplying, laying and jointing of the following sizes of double wall corrugated (DWC) pipes made out of HDPE conforming to IS 14930 Part II for mechanical protection to underground power cables with all required accessories in ground in the existing trench |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.11 | 90.12.12.8 : Supply & laying of DWC pipe in ordinary soil 1.2 m below ground level including excavation |  | 120 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.12 | 10.4.4 : Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required:300 sq. mm |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.13 | 7.10 : Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.14 | 1.21.1 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.15 | 90.16.3.12 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run)32 x 6 mm copper strip |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.16 | 90.16.4.9 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.17 | 90.16.4.11 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run).32 x 6 mm copper strip |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.18 | od249034/2023_2024 : Supply of 11 KV Electrical Rubber Hand Gloves (White) for HT isolation purpose |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.19 | od249035/2023_2024 : Supply and providing plate earthing with 1200x1200x12mm GI earth plate,50 mm GI(medium&lt;br&gt;class) watering pipe,GI funnel with weld mesh,25x5 mm GI clamps,CI/MS cover plate with&lt;br&gt;locking arrangements,charcoal/coke and salt etc including providing brick work masonry&lt;br&gt;enclosure at the top (450x450x450mm inside)etc as required. |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.2 | od249036/2023_2024 : Supply and fixing Emergency push button with enclosure of MS Construction in surface/recess&lt;br&gt;with stainless steel chain &amp;amp; hammer assembly Complete with glass and push button on&lt;br&gt;wall and giving connection etc. as required |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.21 | od246442/2023_2024 : Supply and providing 9 Litre capacity GI Fire Bucket painted in post office red with primer coat&lt;br&gt;of red oxide and written with white paint &apos;FIRE&apos; mounted on MS angle frame work/ wall bracket&lt;br&gt;filled with fine sand, painting the bracket/ floor stand including making good the damages, colour washing etc. as required |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.22 | od246444/2023_2024 : Supply and providing 4/5 Kg. Dry Chemical Powder type Fire Extinguisher with hose and&lt;br&gt;clamps including fixing it to wall as required. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.23 | od246447/2023_2024 : Painting letters or figures with enamel paint as identification mark to SB, DB, panel board etc as required |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.24 | od244851/2023_2024 : Supply and providing 25x3mm brass bolt |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.25 | od244852/2023_2024 : Supply and providing 25x6mm brass bolt |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5 | Lightening protection | [7 empty] | 1
5.01 | 5.4 : Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 9 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.02 | od50/2022_2023 : Providing and fixing 2 x 25mm X 3 mm copper strip test joint for the earthing system. |  | 5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.03 | od51/2022_2023 : Providing and fixing 25mm X 3 mm copper strip earth lead from the test joint to the earth plate. |  | 45 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.04 | od53/2022_2023 : Supply and laying the following sizes of strips laid 0.60 m below ground level including excavating trench of suitable size and refilling etc. as required (in ordinary soil).&lt;br&gt;25 x 3 mm copper strip tinned at the points of contacts |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.05 | 90.16.4.8 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.06 | 90.6.10.3 : Supply and fixing of following sizes of light gauge PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.07 | 90.16.4.16 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 180 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.08 | 90.16.3.19 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6 | Fire Fighting | [7 empty] | 1
6.01 | od48/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : |  | 643 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.02 | od49/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 32mm dia |  | 101 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.03 | od52/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 40 mm dia |  | 195 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.04 | od54/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 50 mm dia |  | 154 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.05 | od55/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 65 mm dia |  | 112 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.06 | od56/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 80 mm dia |  | 173 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.07 | od58/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 100 mm dia |  | 153 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.08 | od59/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 150 mm dia |  | 160 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.09 | od60/2022_2023 : Providing, laying, testing &amp; commissioning of &apos;C&apos; class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : 200 mm dia |  | 8 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.1 | od61/2022_2023 : Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 2000mm dia |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.11 | od62/2022_2023 : Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 150mm dia |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.12 | od64/2022_2023 : Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 100mm dia |  | 13 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.13 | od65/2022_2023 : Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 80mm dia |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.14 | od68/2022_2023 : Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out&lt;br&gt;of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel&lt;br&gt;flange. 200mm dia |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.15 | od70/2022_2023 : Supplying, fixing, testing and commissioning of Non return valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 150mm dia |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.16 | od71/2022_2023 : Supplying, fixing, testing and commissioning of Non return valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 100mm dia |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.17 | od74/2022_2023 : Supplying, fixing, testing and commissioning of Non return valve of PN 1.6 rating with&lt;br&gt;bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets&lt;br&gt;conforming to IS 13095 of following sizes as required : 80mm dia |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.18 | od75/2022_2023 : Providing &amp; fixing of 25mm dia gun metal globe valve |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.19 | od78/2022_2023 : Providing &amp; fixing of 12/15mm dia gun metal globe valve |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.2 | od80/2022_2023 : Providing &amp; fixing of pressure switch in M.S. pipe line including connection etc. as required. |  | 3 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.21 | od81/2022_2023 : Providing, fixing, testing &amp; commissioning of 15mm dia quartzoid bulb type sprinklers of&lt;br&gt;rating 68 degree centigrade with required accessories. Horizontal side wall sprinkler |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.22 | od82/2022_2023 : Providing, fixing, testing &amp; commissioning of 15mm dia quartzoid bulb type sprinklers of&lt;br&gt;rating 68 degree centigrade with required accessories. Pendent Sprinkler |  | 390 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.23 | od83/2022_2023 : Providing &amp; fixing of Providing &amp; fixing of Air Release Valve |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.24 | od84/2022_2023 : Providing &amp; fixing of Pressure Gauge in M.S. pipe line including connection etc. as required |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.25 | od85/2022_2023 : Supplying, installation, testing and commissioning of electric driven pressurisation pump&lt;br&gt;suitable for automatic operation and consisting of following, complete in all respects, as&lt;br&gt;required : (Jockey Pump) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS : 1520. Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-&apos;F&apos; insulation, conforming to IS : 325. M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 180 lpm at 70 m Head |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.26 | od86/2022_2023 : Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height&lt;br&gt;with air release valve on top and flanged connection to riser, drain arrangement with 25 mm&lt;br&gt;dia gun metal wheel valve with required accessories, pressure gauge and paintingwith&lt;br&gt;synthetic enamel paint of approved shade as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.27 | od88/2022_2023 : Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable&lt;br&gt;for automatic operation and consisting of following, complete in all respects, as required :&lt;br&gt;Horizontal type, multistage, centrifugal, split casing pump of cast iron body &amp; bronze&lt;br&gt;impeller with stainless steel shaft, mechanical seal conforming to IS 1520.&lt;br&gt;Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for&lt;br&gt;operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure,&lt;br&gt;horizontal foot mounted type with Class-&apos;F&apos; insulation, conforming to IS-325.&lt;br&gt;M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as&lt;br&gt;required.&lt;br&gt;Suitable cement concrete foundation duly plastered with anti vibration pads.2280 lpm at 70 m Head |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.28 | od89/2022_2023 : Supplying, installation, testing and commissioning of diesel engine driven main fire pump&lt;br&gt;suitable for automatic operation and consisting of following, complete in all respects, as&lt;br&gt;required : (Diesel Driven Pump)Horizontal type, multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS&lt;br&gt;standard complete with auto starting mechanism, 12 /24 volts electric starting equipment,&lt;br&gt;diesel tank, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm&lt;br&gt;thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer,&lt;br&gt;instruments and protection as per standard specification, stop solenoid for auto stop in the&lt;br&gt;event of fault with audio indications, painted with post office red colour etc. as required. M.S fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as&lt;br&gt;required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 2280 lpm at 70 m Head |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.29 | od90/2022_2023 : Fabrication, supply, Insallation testing &amp; commissioning of Electrical control panel of cubical&lt;br&gt;construction, floor mounted type, fabricated out of 2mm thick CRCA sheet,&lt;br&gt;compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of&lt;br&gt;approved shade after 7 tank treatment process, cable alley, inter-connection with suitable&lt;br&gt;size copper conductor cable/solid copper strip, having switchgears and accessories,&lt;br&gt;mountings and internal wiring, earth terminals, numbering etc. complete in all respect,&lt;br&gt;suitable for main fire pump, pressurisation pump &amp; diesel pump set complete as per CPWD&lt;br&gt;specification with following in coming and Outgoings, suitable for operation on 415V, 3&lt;br&gt;phase, 50Hz Ac Supply with enclosure protection class IP 42 as required : |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.3 | od91/2022_2023 : Supplying and fixing single headed internal hydrant valve with instantaneous&lt;br&gt;Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming&lt;br&gt;to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required :.Single headed Stainless steel. |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.31 | od92/2022_2023 : Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia&lt;br&gt;instantaneous FM Gunmetal/Stainless Steel coupling and cast iron wheel, ISI marked,&lt;br&gt;conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required.Single headed Stainless steel |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.32 | od96/2022_2023 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3 X 10 sq. mm |  | 2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.33 | od179525/2024_2025 : Supplying, Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. 3Core X 35Sqmm Aluminium Cable (clamped with 1mm thick saddle)MR |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.34 | od179492/2024_2025 : supplying, laying and fixing of one number PVC insulated and pvc sheathed XLPE power cable of 1.1 KV grade of following size on wall surface as required 3core X 10Sqmm Aluminium cable (clambed with 1mm thick saddle) |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.35 | od97/2022_2023 : Supply, Installation, Testing and Commissioning of Inline Duct Fresh Air fan with speed regulator, Pre-Filter and all necessary supports &amp; fixing arrangement.&lt;br&gt;2450 CFM and 20mm w.g ESP |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.36 | od98/2022_2023 : Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female&lt;br&gt;couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required :Stainless Steel (Grade 304) |  | 28 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.37 | od99/2022_2023 : Supplying &amp; fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal&lt;br&gt;diameter size nozzle conforming to IS 903 suitable for instantaneous connection to&lt;br&gt;interconnect hose pipe coupling as required : Stainless Steel (Grade 304) |  | 14 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.38 | od100/2022_2023 : Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office&lt;br&gt;red, conforming to IS 884 complete with the following as required.&lt;br&gt;20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS:&lt;br&gt;12585&lt;br&gt;20 mm nominal internal dia gun metal globe valve &amp; nozzle.&lt;br&gt;Drum and brackets for fixing the equipmets on wall.&lt;br&gt;Connections from riser with 25 mm dia stop gun metal valve &amp; M.S. Pipe and socket. 30m |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.39 | od101/2022_2023 : Providing &amp; fixing of 5/6 Kg. ABC Stored pressure type fire extinguisher with ISI mark. |  | 9 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.4 | od103/2022_2023 : Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required : 3 way - 150 mm dia M.S. Pipe |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.41 | od104/2022_2023 : Supplying, installation, testing &amp; commissioning of Fire Alarm Panel 8Zone conventional type micro processor based control panel of MS cabinet powder coated audio and visual display with all necessary attachments. |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.42 | od105/2022_2023 : Supplying, installation, testing &amp; commissioning fire alarm sounder with facility to&lt;br&gt;make announcement, mounted in M.S. box (16 SWG) with hinged cover plate &amp;&lt;br&gt;suitable for operation with amplifier i/c line matching transformer etc. complete as&lt;br&gt;required. |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.43 | od106/2022_2023 : Supplying, installation, testing &amp; commissioning of smoke detector with builtin LED&lt;br&gt;and mounting base complete with all connections etc. as required. |  | 166 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.44 | od107/2022_2023 : Supplying, installation, testing &amp; commissioning of heat detector operating at 54&ordm;C/&lt;br&gt;57&ordm;C with rate of rise cum fixed tempreature (dual thermistor) type with mounting&lt;br&gt;base complete with all connection etc. as required. |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.45 | od108/2022_2023 : Supplying, installation, testing &amp; commissioning of manual call boxes of MS&lt;br&gt;construction in surface/recess with stainless steel chain &amp; hammer assembly&lt;br&gt;complete with glass and push button etc. as required. |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.46 | od109/2022_2023 : Supplying &amp; laying of 2x1.5 sqmm fire alarm armoured cable, 600/1000V rated with&lt;br&gt;annealed copper conductor having XLPE insulation, steel wire armouring &amp; FRLS&lt;br&gt;outer sheath complete as required. |  | 4200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.47 | od110/2022_2023 : Supplying, installation, testing &amp; commissioning talk back slave station in surface/&lt;br&gt;recess suitable for operation on simplex mode complete with P.T.T. knob &amp; speaker/ microphone enclosed in a M.S.(16 SWG)/ ABS box with break glass in front etc. complete as required. |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.48 | od112/2022_2023 : Supplying, installation, testing &amp; commissioning of Micro Controller Based 6 ZoneTalk Back System With Builtin Microphone &amp; Builtin Mixer Amplifier With Following Features&lt;br&gt;(a) Feather type key pads to select the zones.&lt;br&gt;(b )Backlight Liquid Crystal Display(LCD)&lt;br&gt;(c) User friendly interactive display.&lt;br&gt;(d) Announcement selector - PTT Switch.&lt;br&gt;(e) Listen selector switch.&lt;br&gt;(f) All Call switch to select all zones simultaneously for announcement&lt;br&gt;(g) Builtin Power supply.&lt;br&gt;(h) Zone Selector Switching Circuit&lt;br&gt;(i)Terminal blocks to terminate zones wires, amplifier wires etc.,&lt;br&gt;(j)Individual volume controles for Announcement &amp; Listen&lt;br&gt;(k) Built in speaker.&lt;br&gt;(l) Built in microphone.&lt;br&gt;(m) Builtin in 60 Watts Amplifier&lt;br&gt;(n) Zones Call Display On the LCD With Audio Alarm.&lt;br&gt;(o) Zone Call processing Circuit |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.49 | od113/2022_2023 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor,&lt;br&gt;single core cable in the existing surface/ recessed steel/ PVC conduit as required. 2 x 1.5 sq. mm |  | 1200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.5 | od114/2022_2023 : Supply and providing fire escape route plan of thea each floor with marking of escape route(Size 600x450 mm size) as per the direction |  | 12 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.51 | od115/2022_2023 : Supplying and fixing of following sizes of medium class PVC conduit along with&lt;br&gt;accessories in surface/recess including cutting the wall and making good the same&lt;br&gt;in case of recessed conduit as required. 20mm |  | 180 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.52 | od116/2022_2023 : Supplying and fixing of following sizes of medium class PVC conduit along with&lt;br&gt;accessories in surface/recess including cutting the wall and making good the same&lt;br&gt;in case of recessed conduit as required.25 mm |  | 180 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.53 | od117/2022_2023 : Supply and errection of Self Glowing Sign boards made out of 3 mm thick PVC foam board size:12&quot;x 4&quot; |  | 29 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.54 | od118/2022_2023 : Supplying and fixing of LED Exit Light 5 mm Clear Acrylic Letter Engraved with Laser 230 V Ac. with battery Back up size : 11 X 4 Inch |  | 21 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.55 | od119/2022_2023 : Supply and errection of Self Glowing Sign boards made out of 3 mm thick PVC foam board size:18x12&quot; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.56 | od120/2022_2023 : DOUBLE DOOR HOSE BOX-Supply &amp; Installation of Double door Hose cabinet |  | 14 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7 | Elevator | [7 empty] | 1
7.01 | od9961/2022_2023 Supply, installation and commissioning of 26Persons Passenger/ Hospital Bed Lift with the following specification : Type of Lift - passenger/Bed Lift (26 Passenger) Gear less , Load / Persons -1768Kg. / 26 persons, Rated speed -1 M/Sec.Travel - 15 Mtr ( Approx ), No. of floor and entrance served - round<br>+3Floor, No. of floor served - Four floors, Method of control - With/without attendant, Position of machine room - Top of lift well, Size of lift well - 320cm x250 cm, Position of counter weight - Any one side of the entrance, Size of car platform - As per ISS, Car entrance - 1200 mm wide x 2000mm height, Drive - Variable voltage variable frequency, Operation - Simplex selective, Construction of design and furnishing of car body work - Stainless steel car with Stainless Steel framed 1/2 glass door, false ceiling, indirect lighting with fan, Stainless steel chequered plate Flooring. Landing entrance - Automatic 2 speed stainless steel door as per ISS with provision for mechanical opening key for emergency, Bell indication and position indicator - Up/down, Electric supply - Light 230/50C/s single phase 2 wire system. Power 415V 50C/s 3 phase 4 wire system., Machine - As per requirement, Infra red door opening system -To be provide for entire length of the door, Automatic Rescue Device - Provide automatic rescue device with an electronic controller powered by suitable size dry free maintenance batteries. The rescue operation<br>within 10 seconds if power failure with announcement , Indication in the car - a)<br>Car position,b) Call indicator,c) Door close/open push button, d) Emergency stop<br>button, e) Flush mounted switch for fan and light, f) Non stop button (All buttons in car and all landings should have Braille sign). g) Battery operated emergency<br>lamp with rechargeable batteries., h) Battery operated alarm bell I) Intercom<br>wiring with one master unit, Winding handle - Manual winding handle for use in,<br>Safeties - a) Over speed governor, operated safety,<br>b) Buffers, c) Motor over<br>load protection, d) Phase reversal protection, e) Other safeties as per ISS, f)<br>Single phase preventor, g) Final limit switch, Leveling - Automatic levelling at all<br>landing, Guarantee - Company shall carry out 36 months free maintenance during warranty period and includes, a) Cleaning lift equipment, b) Lubrication of all moving parts, c) Replacing of lubricating oil when required, d) Checking and<br>adjusting contacts, e) Replacing fusible item alarm etc.f) Recharging batteries in<br>case of drain/ renewing batteries, g ) Replacing /rewinding motors, Control panel - Control panel will be dust and vermin proof of sheet metal enclosure, Announcement System - To provide lift announcement system, Approval - Preparing drawings and obtaining approval from concerned electrical Inspectorate including 1st year insurance . Tests - At site test as per IS to be carried out before Handing over including minor<br>civil work - Buffer concrete, pit water proofing, machine room rope hole drilling etc. |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information