## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: WAPCOS Limited
Work Name : 30 Bedded Integrated AYUSH Hospital Kottarakkara
Contract No: WAP/INFRA/KERALA/2024/GAHK/492
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | CIVIL WORKS | BI01010001010000000000000515BI0100001113 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | 2.6.1 : Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead up to 50 m and lift up to 1.5 m, disposed earth to be levelled and neatly dressed.All kinds of soil |  | 2872.783 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 2.31 : Clearing jungle including uprooting of rank vegetation, grass, brush wood, trees and saplings of girth up to 30 cm measured at a height of 1 m above ground level and removal of rubbish up to a distance of 50 m outside the periphery of the area cleared |  | 1000 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | 2.25 : Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m.Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m. |  | 2296.628 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.04 | 2.26.1 : Extra for every additional lift 1.5 m or part there of in excavation / banking excavated or stacked materials.All kinds of soil |  | 285.163 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.05 | 2.34.1 : Supplying chemical emulsion in sealed containers including delivery as specified.Chlorpyriphos / Lindane emulsifiable concentrate of 20% |  | 391.075 | Litre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.06 | 2.35.3.1 : Diluting and injecting chemical emulsion for POST -CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion):Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1:2 (1 cement : 2 coarse sand) to match the existing floor:With Chlorpyriphos/Lindane E.C. 20% with 1% concentration |  | 782.157 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | 4.11 : Providing and laying damp-proof course 50 mm thick with cement concrete 1:2:4(1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). |  | 94.516 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.08 | od118959/2024_2025 : Providing &amp; applying a coat of residual petroleum bitumen of grade of VG-10&lt;br&gt;of approved quality using 1.7kg per square metre on damp proof course after&lt;br&gt;cleaning the surface with brushes and finally with apiece of cloth lightly&lt;br&gt;soaked in kerosene oil. |  | 94.516 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.09 | 4.1.10 : Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level:1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40 mm nominal size) |  | 171.3 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.1 | 5.9.1 : Centering and shuttering including strutting, etc. and removal of form for:Foundations, footings, bases of columns, etc for mass concrete |  | 474.303 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | 5.9.2 : Centering and shuttering including strutting, etc. and removal of form for:Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. |  | 1921.842 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | 5.9.3 : Centering and shuttering including strutting, etc. and removal of form for:Suspended floors, roofs, landings, balconies and access platform |  | 1493.678 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | 5.9.5 : Centering and shuttering including strutting, etc. and removal of form for:Lintels, beams, plinth beams, girders bressumers and cantilevers |  | 2688.997 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | 5.9.6 : Centering and shuttering including strutting, etc. and removal of form for:Columns, Pillars, Piers, Abutments, Posts and Struts |  | 982.422 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | 5.9.7 : Centering and shuttering including strutting, etc. and removal of form for:Stairs, (excluding landings ) except spiral - staircases) |  | 311.853 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | 5.9.16.1 : Centering and shuttering including strutting, etc. and removal of form for:Edges of slabs and breaks in floors and wallsUnder 20 cm wide |  | 369.75 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | 5.9.19 : Centering and shuttering including strutting, etc. and removal of form for:Weather shade, Chajjas, corbels etc., including edges |  | 288.225 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | 5.22.6 : Steel reinforcement for R.C.C work including straightening, cutting, bending, placing in position and binding all complete upto plinth levelThermo - Mechanically Treated bars of grade Fe-500D or more |  | 38388.7 | kilogram |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | 5.30 : Add for plaster drip course / groove in plastered surface or moulding to R.C.C. projections. |  | 384.301 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | 5.22A.6 : Steel reinforcement for R.C.C work including straightening, cutting, bending, placing in position and binding all complete above plinth level.Thermo - Mechanically Treated bars of grade Fe-500D or more |  | 82822.302 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | 5.33.1 : Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer - in-charge. Note:- Cement content considered in this item is @ 330 kg/ cum. Excess or less cement used as per design mix is payable or recoverable separately.All work upto plinth level |  | 409.378 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | 5.34.1 : Extra for providing richer mixes at all floor levels. Note:- Excess/less cement over the specified cement content used is payable/ recoverable separately.Providing M-30 grade concrete instead of M-25 grade BMC/RMC. (Note:- Cement content considered in M-30 is @ 340 kg/cum). |  | 104.499 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | 5.33.2 : Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer - in-charge. Note:- Cement content considered in this item is @ 330 kg/ cum. Excess or less cement used as per design mix is payable or recoverable separately.All work above plinth level upto floor V level |  | 680.177 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | 5.1.2 : Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level:1:1:5:3 (1 cement 1.5 coarse sand :3 graded stone aggregate 20 mm nominal size |  | 346.322 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | 6.13.1 : Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:3 (1 cement : 3 coarse sand) |  | 228.799 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | 6.15 : Extra for providing and placing in position 2 Nos 6 mm dia M.S bars at every third course of half brick masonry. |  | 521.438 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | 50.6.1.4 : Solid block masonry using pre cast solid blocks (Factory made) of size 30x20x20cm or nearest available size confirming to IS 2185 part I of 1979 for foundation and plinth with thickness 20cm and above in: CM 1:6 ( 1 cement : 6 coarse sand ) etc complete |  | 29.089 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | 50.6.1.5 : Solid block masonry using pre cast solid blocks ( Factory made) of size 30x20x20cm or nearest available size confirming to IS 2185 Part I of 1979 for super structure up to floor two level thickness 20cm and above in: CM 1:6 ( 1 cement : 6 coarse sand) etc complete |  | 404.851 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | 50.6.1.6 : Solid block masonry using pre cast solid blocks (Factory made) of size 30x20x20cm or nearest available size confirming to IS 2185 part I of 1979 for super structure above floor two level upto floor five level thickness 20cm and above in : CM 1:6 ( 1 cement : 6 coarse sand sand) etc complete |  | 62.653 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | 9.48.2 : Providing and fixing M.S. Grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete.Fixed to openings/ wooden frames with rawl plugs screws etc |  | 1398 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | 13.1.1 : 12 mm cement plaster of mix:1:4 ( 1 cement : 4 fine sand) |  | 4497.659 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | 13.2.1 : 15 mm cement plaster on the rough side of single or half brick wall of mix:1:4 (1 cement :4 fine sand) |  | 1917.644 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | 13.10 : 15 mm cement plaster 1:3 ( 1 cement :3 coarse sand) finished with a floating coat of neat cement on the rough side of single or half brick wall. |  | 648.226 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | 13.16.1 : 6 mm cement plaster of mix:1:3 ( 1 cement : 3 fine sand) |  | 1955.154 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | 13.22 : Extra for plastering exterior walls of height more than 10 m from ground level for every additional height of 3 m or part thereof. |  | 449.46 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.36 | 11.39 : Providing and laying rectified Glazed Ceramic floor tiles of size 300x300 mm or more (thickness to be specified by the manufacturer), of 1st quality conforming to IS: 15622, of approved make in colours White, Ivory, Grey, fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 cement : 4 Coarse sand), including grouting the joints with white cement and matching pigments etc., complete. |  | 112.521 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.37 | 11.41.2 : Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20 mm thick cement mortar 1:4(1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600 x 600 mm. |  | 1409.523 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.38 | 11.46.2 : Providing and laying Vitrified tiles indifferent sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm |  | 98.044 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.39 | 11.19.4 : Chequered terrazo tiles 22 mm thick with graded marble chips of size up to 6 mm in floors, jointed with neat cement slurry mixed with pigment to match the shade of the tiles, including rubbing and polishing complete, on 20 mm thick bed of cement mortar 1:4 ( 1 cement : 4 coarse sand):Ordinary cement without any pigment |  | 205.951 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.4 | 8.2.2.2 : Providing and fixing 18 mm thick gang saw cut, mirror, polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations, of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 ( 1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels.Area of slab over 0.50 sqm |  | 152.46 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.41 | 8.3.2 : Providing edge moulding to 18 mm thick marble stone counters, vanities etc., including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer -in-Charge.Granite work |  | 424.2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.42 | 8.31 : Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineerin-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 486.38 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.43 | 13.43.1 : Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface:Water thinnable cement primer |  | 6215.573 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.44 | 13.47.1 : Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade:New work (Two or more coats applied @ 1.43 ltr/ 10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) |  | 1917.644 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.45 | 13.60.1 : Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade:Two or more coats on new work |  | 6215.573 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.46 | 13.61.1 : Painting with synthetic enamel paint of approved brand and manufacture to give an even shade:Two or more coats on new work |  | 109.904 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.47 | 13.68.1 : French spirit polishing:Two or more coats on new works including a coat of wood filler |  | 311.285 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.48 | 9.1.1 : Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately).Second class teak wood |  | 1.674 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.49 | 9.5.1.1 : Providing and fixing panelled or panelled and glazed shutters for shutters for doors, windows and clerestory windows, including ISI marked M.S. pressed butt hinges bright finished of required size with necessery screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer - in-charge.Second class teak woodProviding and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note:- Butt hinges and necessary screws shall be paid separately) Second class teak wood 35 mm thick shutters |  | 97.442 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.5 | 9.7.1 : Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured), Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick:Second class teak wood |  | 111.004 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.51 | 21.1.1.2 : Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS : 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminnium snap beading for glazing /paneling, C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge.(Glazing, paneling and dash fasteners to be paid for separately):For fixed portionPowder coated aluminium (minimum thickness of powder coating 50 micron) |  | 430.5 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.52 | 21.1.2.2 : For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber/ neoprene gasket required (Fittings shall be paid for separately)Powder coated aluminium (minimum thickness of powder coating 50 micron) |  | 506.581 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.53 | 21.3.1 : Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of Engineer - in -Charge. ( Cost of aluminium snap beading shall be paid in basic item):With float glass panes of 4.0 mm thickness |  | 66.03 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.54 | 21.18 : Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc to be paid separately) |  | 4.2 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.55 | 21.3.2 : Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of Engineer - in -Charge. ( Cost of aluminium snap beading shall be paid in basic item):With float glass panes of 5.50 mm thickness |  | 19.8 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.56 | 10.28 : Providing and fixing stainless steel (Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners, stainless steel bolts etc., of required size on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.) |  | 569.979 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.57 | 21.19.1 : Filling the gap in between aluminium/ stone/ wood frame and adjacent RCC/ Brick/ Stone/ wood/ Ceramic/ Gypsum work by providing weather/structural non sag elastomeric PU sealant over backer rod of approved quality as per architectural drawings and direction of Engineer-in-charge complete, complying to ASTM C920, DIN 18540-F & ISO 11600Upto 5 mm depth and 5 mm width |  | 335.2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.58 | 9.105.1 : Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with Zinc coating of 120 gms/ (both side inclusive), consisting of floor and ceiling channel 50 mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete.75 mm overall thickness partition with 12.5 mm thick double skin fire rated board conforming to IS : 2095 : part I |  | 138.461 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.59 | 9.117.2 : Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1 mm), with wall thickness 2.0mm (±0.2 mm), corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joints mitred and plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 x 19 mm and 1 mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer's specification and direction of Engineer-in-chargeExtruded section profile size 42x50 mm |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.6 | 9.118.1 : Providing and fixing to existing door frames24 mm thick factory made PVC door shutters made of styles and rails of a uPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2 mm) with inbuilt edging on both sides. The styles and rails mitred and joint at the corners by means of M.S. galvanised/plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanised M.S. tube of size 20x20 mm and 1 mm (± 0.1 mm) wall thickness. The lock rail made up of 'H' section, a uPVC hollow section of size 100x24 mm and 2 mm (± 0.2 mm) wall thickness,fixed to the shutter styles by means of plastic/galvanised M.S. 'U' cleats. The shutter frame filled with a uPVC multi-chambered single panel of size not less than 620 mm, having over all thickness of 20 mm and 1 mm (± 0.1 mm) wall thickness. The panels filled vertically and tie bar at two places by inserting horizontally 6 mm galvanised M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer-in-charge( For W.C. and bathroom door shutter). |  | 67.2 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.61 | 9.53 : Providing 40x5 mm flat iron hold fast 40 cm long including fixing to frame with 10 mm diameter bolts, nuts and wooden plugs and embeddings in cement concrete block 30x10x15 cm 1:3:6 mix ( 1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) |  | 252 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.62 | 9.70.2 : Providing and fixing IS : 12817 marked stainless steel butt hinges with stainless steel screws etc. complete:100x58x1.90 mm |  | 336 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.63 | 9.97.3 : Providing and fixing aluminium tower bolts, ISI marked, anodised(anodic coating not less than grade AC 10 as per : 1868), transparent or dyed to required colour or shade, with necessary screws complete:200x10 mm |  | 84 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.64 | 9.100.1 : Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete:125 mm |  | 84 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.65 | 9.100.3 : Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete:75 mm |  | 210 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.66 | 9.101.1 : Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete.Single rubber stopper |  | 25 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.67 | 9.102 : Providing and fixing aluminium casement stays, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. |  | 126 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.68 | 9.103 : Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS: 1868) aluminium lever handles of approved quality with necessary screws etc . complete. |  | 42 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.69 | 9.161 : Providing and fixing fire resistant door frame of section 50 x 60 mm on horizontal side & 35 x 60 mm on vertical sides having built in rebate made out of 1.6 mm thick GI sheet ( Zinc coating not less than 120gm/m2) suita2ble for mounting 120 min Fire Rated Glazed Door Shutters. The frame shall be filled with Mineral wool Insulation having density min 96Kg/m2 . The frame will have a provision of G.I. Anchor fastners 14 nos ( 5 each on vertical style & 4 on horizontal style of size M10 x 80 ) suitable for fixing in the opening along with Factory made Template for SS Ball Bearing Hinges of Size 100x89x3mm for fixing of fire rated glazed shutter . The frame shall be finished with a approved fire resistant primer or Powder coating of not less than 30 micron in desired shade as per the directions of Engineer - in- charge . (Cost of SS ball bearing hinges is excluded |  | 16.201 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.7 | 9.162 : Providing and fixing 60 mm thick glazed fire resistant door shutters of 120 min Fire Rating confirming to IS:3614 (Part II) or EN1634-1:1999, tested and certified as per laboratory approved by Engineer-in-charge, with suitable mounting on door frame, consisting of vertical styles, top rail & side rail 60 mm x 60 mm wide and bottom rail of 110 mm x 60 mm made out of 1.6mm thick G.I. sheet (zinc coating not less than 120gm/m²) duly filled mineral wool insulation having density min 96 kg/m³ and fixing with necessary stainless steel ball bearing hinges of size 100x89x3mm of approved make, including applying a coat of approved fire resistant primer or powder coating not less than 30 micron etc all complete as per direction of Engineer-in-charge (panelling to be paid for seperately |  | 7.561 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.71 | od118983/2024_2025 : Fabricating, suppling and fixing 300mm high, 50mm deep embossed acrylic letters, as per design on the wall, including LED lights in required number in such letters with all wiring and accessories including design, drawing and direction of Engineer-at-site.. |  | 10.5 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.72 | od118984/2024_2025 : NAME BOARD ACP SHEET WITH MULTIWOOD LETTERING : Design, Supplying and fixing Name Board as per the technical specifications given -1 Inch GI pipe frame (16Guage) for Frame (Size proportional), Primer Paint &amp; Black Painted Pipes for Frame.,5mm ACP sheets (Aluminum Composite Panel) for Box area, 18mm thick Multi wood Lettering for Name Board as approved by Engineer in charge. For Measurement purpose, only area of ACP sheet to be measured.&lt;br&gt; |  | 5.601 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.73 | od118985/2024_2025 : od81326/2021_2022&lt;br&gt;Supply and fixing of Signage Boards inc. main institutional boards and name boards&lt;br&gt; |  | 1 | L.S |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.74 | od119813/2024_2025 : Supply and erection of airport chairs manufactured by prime quality of CRCA (Cold Rolled Close Annealed) perforated GI,high quality mild steel powder coated with thickness of 1.4 mm |  | 15 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.75 | od118986/2024_2025 : od159735/2021_2022&lt;br&gt;Supply and installation of Water Dispenser with RO+UV+UF+Taste Enhancer (Purification CartridgesPre Filter,Sediment Filter,Pre-Activated carbon Absorber, RO Membrane, UV Disinfection Column,UF&lt;br&gt;membrane, Post Carbon Cartridge etc.) |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.76 | od118987/2024_2025 : Supplying and fixing Sliding Curtains with all fitting accessories. |  | 113.104 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | Landscaping | [7 empty] | 1
2.01 | 30.2.10.2 : Grassing with selection No. 1 grass including watering and maintenance of the lawn for 60 days or more till the grass forms a thick lawn, free from weeds and fit for mowing including supplying good earth, if needed (the grass and good earth shall be paid for separately).With grass Turf |  | 3200 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.02 | 30.2.50 : Providing & fixing of White River (Stone) Pables size of 2" to 2.50" dia in natural colour at site of work including loading, unloading, carriage and all taxes paid etc.and as per direction of officer in charge. |  | 200 | quintal |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | 30.2.57.1 : Plantation of Trees, Shrubs, and Hedge at site i/c watering and removal of unsaverieable material?s as per direction of officer in charge (excluding cast of plant & water )Cost of plantation per trees plants (for 100 nos.=427.45/100) |  | 1715 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | 16.68 : Providing and laying 60 mm thick factory made cement concrete interlocking paver block of M - 30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50 mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. |  | 915 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | 20 KLD STP - CIVIL WORKS | [7 empty] | 1
3.01 | 2.8.1 : Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift up to 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m.All kinds of soil |  | 143.705 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.02 | 2.26.2 : Extra for every additional lift 1.5 m or part there of in excavation / banking excavated or stacked materials.Ordinary or hard rock |  | 143.705 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.03 | 2.32 : Clearing grass and removal of the rubbish up to a distance of 50 m outside the periphery of the area cleared. |  | 51.5 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.04 | 5.9.1 : Centering and shuttering including strutting, etc. and removal of form for:Foundations, footings, bases of columns, etc for mass concrete |  | 7.181 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.05 | 5.9.2 : Centering and shuttering including strutting, etc. and removal of form for:Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. |  | 352.772 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.06 | 5.9.5 : Centering and shuttering including strutting, etc. and removal of form for:Lintels, beams, plinth beams, girders bressumers and cantilevers |  | 4.5 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.07 | 5.9.19 : Centering and shuttering including strutting, etc. and removal of form for:Weather shade, Chajjas, corbels etc., including edges |  | 10.78 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.08 | 5.22.6 : Steel reinforcement for R.C.C work including straightening, cutting, bending, placing in position and binding all complete upto plinth levelThermo - Mechanically Treated bars of grade Fe-500D or more |  | 5878.5 | kilogram |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.09 | 5.22A.6 : Steel reinforcement for R.C.C work including straightening, cutting, bending, placing in position and binding all complete above plinth level.Thermo - Mechanically Treated bars of grade Fe-500D or more |  | 112.501 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.1 | od118963/2024_2025 : Providing and laying in position machine batched and machine mixed design mix&lt;br&gt;M-30 grade cement concrete for reinforced cement concrete work, using cement&lt;br&gt;content as per approved design mix, including pumping of concrete to site of laying&lt;br&gt;but excluding the cost of centering, shuttering, finishing and reinforcement,&lt;br&gt;including admixtures in recommended proportions as per IS: 9103 to accelerate,&lt;br&gt;retard setting of concrete, improve workability without impairing strength and&lt;br&gt;durability as per direction of Engineer-in-charge.&lt;br&gt;All works upto plinth level |  | 16.88 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.11 | od118965/2024_2025 : Providing and laying in position machine batched and machine mixed design mix&lt;br&gt;M-30 grade cement concrete for reinforced cement concrete work, using cement&lt;br&gt;content as per approved design mix, including pumping of concrete to site of laying&lt;br&gt;but excluding the cost of centering, shuttering, finishing and reinforcement,&lt;br&gt;including admixtures in recommended proportions as per IS: 9103 to accelerate,&lt;br&gt;retard setting of concrete, improve workability without impairing strength and&lt;br&gt;durability as per direction of Engineer-in-charge.&lt;br&gt;All works above plinth level upto floor V level |  | 37.135 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.12 | 5.33.2 : Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer - in-charge. Note:- Cement content considered in this item is @ 330 kg/ cum. Excess or less cement used as per design mix is payable or recoverable separately.All work above plinth level upto floor V level |  | 1.19 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.13 | 50.6.1.5 : Solid block masonry using pre cast solid blocks ( Factory made) of size 30x20x20cm or nearest available size confirming to IS 2185 Part I of 1979 for super structure up to floor two level thickness 20cm and above in: CM 1:6 ( 1 cement : 6 coarse sand) etc complete |  | 9.003 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.14 | 13.1.1 : 12 mm cement plaster of mix:1:4 ( 1 cement : 4 fine sand) |  | 55.78 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.15 | 13.2.1 : 15 mm cement plaster on the rough side of single or half brick wall of mix:1:4 (1 cement :4 fine sand) |  | 192.758 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.16 | 13.7.2 : 12 mm cement plaster finished with a floating coat of neat cement of mix:1:4 ( 1 cement : 4 fine sand) |  | 177.396 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.17 | 13.43.1 : Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface:Water thinnable cement primer |  | 45 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.18 | 13.60.1 : Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade:Two or more coats on new work |  | 55.78 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.19 | 13.47.1 : Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade:New work (Two or more coats applied @ 1.43 ltr/ 10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) |  | 43.78 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.2 | 19.7.2.1 : Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand) with R.C.C. top with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size,) inside plastering 12 mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) finished with a floating coat of neat cement complete as per standard design:Inside size 120x90 cm and 90 cm deep including C.I. cover with frame ( medium duty ) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg ( weight of cover 58 kg and weight of frame 58 kg):With common burnt clay F.P.S ( non modular) bricks of class designation 7.5 |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.21 | 19.8.2.1 : Extra for depth for manholesSize 120x90 cmWith common burnt clay F.P.S. ( non modular ) bricks of class designation 7.5 |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4 | Approvals | [7 empty] | 1
4.01 | od118952/2024_2025 : Application and Approval of Building Permit , PCB Approvals, fire NOC Inspectorate Charge for Approval and sanction, KSEB Charge for availing Regularizing the existing HT Connection to New Demand including meter testing Fee etc.. (Actual amount will be reimbursed on submission of receipts)&lt;br&gt; |  | 1 | L.S |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5 | SANITARY FIXTURES, BATH FITTINGS AND ACCESSORIES | [7 empty] | 1
5.01 | 17.2.2 Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required:W.C. pan with ISI marked black solid plastic seat and lid |  | 35 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.02 | 17.7.4 Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require:White Vitreous China Flat back wash basin size 550x400mm with single 15 mm C.P.brasspillar taps |  | 40 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.03 | 17.7.9 Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require:White Vitreous China Surgeon Type wash basin of size 660x460 mm with single 15 mm C P. brass pillar taps with elbow operated levers ISI marked |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.04 | 17.23 Providing and fixing white vitreous china flat back or wall corner type lipped front urinal basin of 430x260x350 mm or 340x410x265 mm sizes respectively. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.05 | 17.31 Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.06 | 17.71 Providing and fixing PTMT liquid soap container 109 mm wide, 125 mm high and 112 mm distance from wall of standard shape with bracket of the same materials with snap fittings of approved quality and colour, weighing not less than 105 gms |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.07 | 17.72 Providing and fixing PTMT towel ring trapezoidal shape 215 mm long, 200 mm wide with minimum distances of 37 mm from wall face with concealed fittings arrangement of approved quality and colour, weighing not less than 88 gms |  | 40 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.08 | 17.75 Providing and fixing PTMT 15 mm Urinal spreader size 95x69x100 mm with 1/2" BSP thread and shapes, weighing not less than 60 gms. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.09 | 17.76.1 Providing and fixing PTMT urinal cock of approved quality and colour.15 mm nominal bore, 80 mm long 42 mm high and 30 mm wide with BSP female threads weighing not less than 48 gms. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.1 | 50.17.1.3 Supplying and fixing CP Towel rod 60cm or nearest available length including cost of materials and labour charges etc complete as per the direction of site Engineer-in-charge. |  | 36 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.11 | 50.17.1.5 Supplying and fixing CP Health Faucet superior quality ( Jagur or equvalent make ) including cost of materials and labour charges etc complete as per the direction of site Engineer-in-charge. |  | 36 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.12 | 8.10.2 Providing and fixing stone slab with table rubbed, edges rounded and polished, of size 75x50 cm deep and 1.8 cm thick, fixed in urinal partitions by cutting a chase of appropriate width with chase cutter and embedding the stone in the chase with epoxy grout or with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 6 mm nominal size) as per direction of Engineer-in Charge and finished smooth.Granite Stone of approved shade |  | 2 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.13 | 18.21.2.1 Providing and fixing uplasticised PVC connection pipe with brass unions:45 cm length15 mm nominal bore |  | 81 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.14 | 18.51.1 Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore |  | 21 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.15 | 18.53.1 Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS: 893115 mm nominal bore |  | 147 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.16 | od124277/2023_2024 Providing and fixing sanitary fixtures for handicapped toilet including one number Extended wall mount closet with soft close seat cover and cistern one wash basin, one pair mounting brackets,one number elbow operated pillar cock and all other related fittings like waste coupling one number hinged rail 76 cm & 4 nos. of grab rails 60cm etc designed for people with special needs comes with as per manufactures specification including cutting and making good the walls and floors wherever required as per drawing and as directed by Engineer in charge. <br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.17 | od124278/2023_2024 "Providing and fixing of Black colour Poly Propylene Laboratory Sink, Dimensions: external 558 x 355 x 240mm, Net weight: 2.7 kg, Temperature range: 0-80°C, 1/2” BSP Waste connection, Net weight: 0.2 kg Dimensions: Ø73, 1½” BSP with PTMT/PP waste coupling, adjustable screw on nut. , including cutting and making good the walls wherever required: Polypropylene Laboratory Sink without drain board<br>"<br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.18 | od124279/2023_2024 Providing and fixing CP Surgical Purpose Elbow Action, Wall Mounted type, Clinical Sink Mixer with extended lever handle, complete with Wall Flanges and all necessary accessories, all as per manufacturer's instructions and to the approval of the Engineer-in-charge.<br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.19 | od124280/2023_2024 Providing and fixing CP Surgical Purpose Elbow Action, Wall Mounted type, Clinical Sink tap with extended lever handle, complete with Wall Flanges and all necessary accessories, all as per manufacturer's instructions and to the approval of the Engineer-in-charge.<br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.2 | od124281/2023_2024 Supplying and fixing CP Health Faucet superior quality ( Jagur or equvalent make ) including cost of materials and labour charges etc complete as per the direction of site Engineer-in-charge.<br> |  | 36 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.21 | od124282/2023_2024 "Providing and Fixing ABS Body P-Trap with threaded union connections, flanges and all other necessary accessories, all as per manufacturer's instructions and to the approval of the Engineer-in-charge.<br>For Wash Basin, 32mm, Size."<br> |  | 43 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.22 | od124283/2023_2024 "Providing and Fixing ABS Body P-Trap with threaded union connections, flanges and all other necessary accessories, all as per manufacturer's instructions and to the approval of the Engineer-in-charge.<br>For Sinks and Scrub, 40mm, Size"<br> |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.23 | od124284/2023_2024 Supplying and fixing CP Towel rod 60cm or nearest available length including cost of materials and labour charges etc complete as per the direction of site Engineer-in-charge.<br> |  | 36 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.24 | od124285/2023_2024 Providing and fixing of C. P. Robe Hook, 60mm. Dia. x 45mm. High. <br> |  | 36 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.25 | od124286/2023_2024 "Providing,fixing testing and commissioning Energy Efficient Storage Type Electric Water Heater, 2kw each, as per specification<br>Capacity 15 Ltrs"<br> |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.26 | od124287/2023_2024 Providing and fixing cooler (hot, cold and normal water) with inbuild RO filter including cost and conveyance of all materials labour charges etc. complete, including necessary wall cutting / chasing and making good as required etc. complete, testing and commissioning to the satisfaction of Engineer in Charge as per direction of Engineer-In charge at all levels.<br> |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6 | INTERNAL DRAINAGE | [7 empty] | 1
6.01 | 50.18.8.6.2 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc. 50 mm pipe 6 kgf/cm2 |  | 92 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.02 | 50.18.8.7.2 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc 63 mm pipe 4 kgf/ cm2 |  | 105 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.03 | 50.18.8.8.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc. 75 mm pipe 6 Kgf/cm2 |  | 138 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.04 | 50.18.8.9.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chased and making good the wall etc. 110 mm pipe 6kgf/cm2 |  | 22 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.05 | 50.18.9.20.7 Providing and fixing PVC moulded fittings/ accessories for Rigid PVC pipes, including jointing with PVC solvent cement - 63 mm dia vent cowl |  | 154 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.06 | 50.18.9.21.7 Providing and fixing PVC moulded fittings/ accessories for Rigid PVC pipes, including jointing with PVC solvent cement - 75 mm dia Vent cowl |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.07 | 50.18.9.22.8 Providing and fixing PVC moulded fittings /accessories for Rigid PVC pipes, including jointing with PVC solvent cement -110 mm dia Vent cowl |  | 6 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.08 | od124403/2023_2024 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps/clips at 1.00 m spacing. This included jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 75 mm dia 6Kgf/cm2 - External work- Exposed on wall<br> |  | 78 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.09 | od124404/2023_2024 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps/ clips/ at 1.00 m spacing . This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 110 mm dia 6 Kgf/cm2 - External work- Exposed on wall<br> |  | 88.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.1 | od124405/2023_2024 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps/clips at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 63 mm dia 4 Kgf/cm2- External work - exposed on wall<br> |  | 88.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.11 | od124406/2023_2024 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps/Clips at 1.00 m spacing. This included jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 75 mm dia 4 Kfg/cm2 - External work - Exposed on wall<br> |  | 16.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.12 | od124407/2023_2024 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps/clips at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 110 m dia 4 Kgf/cm2 - External work - Exposed on wall<br> |  | 5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.13 | od124408/2023_2024 uPVC fabricated Multi floor trap - Providing, Fixing, testing and commissioning at site in position uPVC Fabricated Multi Floor Trap, with thrust block support including complete cost o cutting chases and making good the walls in all respects - 50/75 mm dia inlet/outlet (In Sunken)<br> |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.14 | od124409/2023_2024 Supplying, installing, testing & commissioning at site in position 110mm dia deep seal PVC P Trap with boss tee and access cap including all necessary fittings and supports complete.<br> |  | 56 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.15 | od124410/2023_2024 Stainless steel Square Flat cut lock grating cover - Providing and Fixing Heavy Duty Stainless Steel Square Flat cut lock Trap Stainless Steel A ISI 304 with 125x125 mm. Grating, for 110mm. <br> |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.16 | od124411/2023_2024 Heavyduty stainless steel cover for Concealed Floor Trap for Urinal - Providing and Fixing 125x125mm dia Heavyduty stainless steel cover for Concealed Floor Trap ISI 304 Cover, for Urinal.<br> |  | 56 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.17 | od124412/2023_2024 Heavy duty stainless steel cleanout cover - Providing and Fixing Heavy Duty Stainless Steel A ISI 304 Clean out Cover, sealed, threaded covers, including suitable keys for opening, if required. - For 110mm<br> |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.18 | od124413/2023_2024 Heavy duty stainless steel cleanout cover - Providing and Fixing Heavy Duty Stainless Steel A ISI 304 Clean out Cover, sealed, threaded covers, including suitable keys for opening, if required. - For 75mm<br> |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.19 | od124414/2023_2024 "Supply, fix at site in position, Rain Khurra (Rain Water Outlet) Side Wall Parapet Type in Cast Iron body, Aluminium Gratings, S.S. Screws etc. complete with Gratings, all as per Technical Specifications.<br>100mm dia. for 110mm. PVC Down Pipe"<br> |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.2 | od124415/2023_2024 "Supply, fix at site in position, Rain Khurra (Rain Water Outlet) Dome Type with Cast Iron body, Aluminium Ring, Aluminium Dome, S.S. Screws etc. complete with Gratings, suitable for 110mm. of down pipes.<br>100mm dia. for 110mm. PVC Down Pipe"<br> |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7 | WATER SUPPLY | [7 empty] | 1
7.01 | 18.7.2 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall20 mm nominal outer dia pipes |  | 242.8 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.02 | 18.7.3 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall25 mm nominal outer dia pipes |  | 143.2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.03 | 18.7.4 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall32 mm nominal outer dia pipes |  | 11.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.04 | 18.7.5 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall40 mm nominal outer dia pipes |  | 94.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.05 | 18.7.6 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall50 mm nominal outer dia pipes |  | 93.6 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.06 | 18.8.2 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes& fittings, with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc.20 mm nominal outer dia pipes |  | 222 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.07 | 18.9.2 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer- in-Charge. External work20 mm nominal outer dia pipes |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.08 | 18.9.3 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer- in-Charge. External work25 mm nominal outer dia pipes |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.09 | 18.9.4 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer- in-Charge. External work32 mm nominal outer dia pipes |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.1 | 18.9.5 Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer- in-Charge. External work40 mm nominal outer dia pipes |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.11 | 50.18.8.3.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc. 25 mm pipe 12 kgf/cm2 |  | 22.5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.12 | 50.18.9.3.2 Providing and fixing PVC pipes includes jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. 25 mm dia 10KGF/cm2 |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.13 | 50.18.9.4.1 Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge.32 mm dia 10.Kgf/cm2 |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.14 | 50.18.9.5.1 Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching refilling & testing of joints complete as per direction of Engineer in Charge 40 mm dia 10Kgf/cm2 |  | 55 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.15 | 50.18.9.6.1 Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. 50 mm dia 10Kgf/cm2 |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.16 | 50.18.9.13.2 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 25 mm dia 10 Kgf/cm2- External work - Exposed on wall |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.17 | 50.18.9.14.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 32 mm dia 10 Kgf/cm2 - External work- Exposed on wall |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.18 | 50.18.9.15.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 40 mm dia 10Kgf/cm2- External work- Exposed on wall |  | 44.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.19 | 50.18.9.16.1 Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 50 mm dia 10Kgf/cm2 - External work - Exposed on wall |  | 44.4 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.2 | 18.17.2 Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :32 mm nominal bore |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.21 | 18.17.3 Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :40 mm nominal bore |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.22 | 18.17.4 Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50 mm nominal bore |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.23 | 18.18.2 Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete:20 mm nominal bore |  | 32 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.24 | 18.18.3 Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete:25 mm nominal bore |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.25 | od124465/2023_2024 CI Y Strainer 2” (50mm) dia - Supply,Installation,Testing and Commisioning of CI Y-type stainer with drain plug, SS screen 304 complete in all respects.<br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.26 | od124466/2023_2024 CI Y Strainer 1 1/2” (40mm) dia - Supply,Installation,Testing and Commisioning of CI Y-type stainer with drain plug, SS screen 304 complete in all respects.<br> |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.27 | od124467/2023_2024 Brass Automatic Air Release Valves - Providing, Fixing, testing and commissioning at site in positions Brass Automatic Air Release Valves, of approved quality and make on the top of the vertical water supply pipes as per specification and drawing - 3/4"(20mm) dia<br> |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8 | EXTERNAL SEWERAGE & STORM WATER DRAIN | [7 empty] | 1
8.01 | 50.18.9.8.1 Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. 75 mm dia 6 Kgf/ cm2 |  | 120 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.02 | 50.18.9.9.1 Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of Joints complete as per direction of engineer in charge.110 mm dia 6Kgf/cm2 |  | 120 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.03 | 50.18.9.9.2 Providing and fixing PVC pipes includes joints of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in CHarge. 110 mm dia 4 Kg/cm2 |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.04 | 19.4.1.1 Providing and fixing square-mouth S.W. gully trap class SP -1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design:100x100 mm size P typeWith common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.05 | 19.7.1.1 Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand) with R.C.C. top with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size,) inside plastering 12 mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) finished with a floating coat of neat cement complete as per standard design:Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weigh of cover 23 kg and weight of frame 15 kg):With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.06 | 19.8.1.1 Extra for depth for manholesSize 90x80 cmWith common burnt clay F.P.S. ( non modular ) bricks of class designation 7.5 |  | 9 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.07 | 19.16 Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS: 10910 on 12 mm dia steeel bar conforming to IS:1786, having minimum cross section as 23 mm x 25 mm and over all minimum length 263 mm and width as 165 mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufactures permanent identification mark to be visible even after fixing including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1cement: 3 coarse sand: 6 graded stone aggregate 20 mm nominal size)Complete as per design |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.08 | 19.32.1 Making soak pit 2.5 m diameter 3.0 metre deep with 45 x 45 cm dry brick honey comb shaft with bricks and S.W. drain pipe 100 mm diameter, 1.8 m long complete as per standard design.With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.09 | 19.33 Constructing soak pit 1.20x1.20 m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9 | PLUMBING PUMPS AND TANK | [7 empty] | 1
9.01 | 18.48 Providing and placing on terrace (at all floor levels) polyethylene water storage tank :ISI 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. |  | 3000 | Litre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10 | PLUMBING PUMPS | [7 empty] | 1
10.01 | od124734/2023_2024 Supplying, Installing, Testing & Commissioning at site in position of Three Phase Openwell Submersible Pumpsets (1W+1S) having SS Shaft, CI/Bronze Impeller and Cast Iron / Stainless Steel Body, Mechanical Seal. Pumps should be capable to deliver 120 LPM @ 20mtr head each, Head range 15 to 25mtrs.<br> |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.02 | od124735/2023_2024 Supplying, Installing, Testing & Commissioning at site in position of Three Phase Openwell Submersible Pumpsets (1W+1S) having SS Shaft, CI/Bronze Impeller and Cast Iron / Stainless Steel Body, Mechanical Seal. Pumps should be capable to deliver 120 LPM @ 20mtr head each, Head range 15 to 25mtrs.<br> |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11 | Electrification | BI01010001010000000000000515BI0100001114 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11.001 | 1.10.3 : Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.Group C |  | 426 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11.002 | 1.11 : Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. |  | 10 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
11.003 | od119275/2024_2025 : Wiring combined plug point together with the light point/ fan point/ exhaust fan point/ call bell point including 6 A 5 pin modular socket controlled by 6A one way modular switch in the existing switch board and giving connection to the phase,neutral and earth terminal with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable ( Green wire for earthing) etc as required. |  | 82 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.004 | 1.7.1 : Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire |  | 750 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.005 | 90.3.19.3 : Supply conveyance, installation, testing and commissioning the light fittings of following types made from CRCA sheet 0.5mm thickness with all accessories and lamps directly on wall and giving connections with 16/0.20 mm 3 core PVC insulated and sheathed round copper conductor flex wire or extending the original wiring and giving connections as required |  | 231 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.006 | od120525/2024_2025 : Supply conveyance, installation, testing and commissioning the 17 W LED Mirror light fittings directly fixed on wall and giving connections with 16/0.20 mm 3 core PVC insulated and sheathed round copper conductor flex wire or extending the original wiring and giving connections as required (Philips Ultron 17- Watt Wall Light (Cool White, Round, Metal) or its equivalent make. |  | 38 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.007 | 1.58 : Supplying and fixing PVC batten/ angle holder including connection etc. as required. |  | 52 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.008 | od119276/2024_2025 : Supply and Installing B22 type 9W LED Bulb of 100 lumen/watt with PF 0.95. |  | 58 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.009 | od120527/2024_2025 : Supply ,installation,testing and commissioning of 700lm pressure die cast housing Bulk head with IP66 protection &amp; IK 08 having efficacy not less than 105lm/W and giving connection with 3 core flex wire as required.&lt;br&gt;&lt;br&gt; |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.01 | 90.4.1 : Supply and installation of suitable size MS rod type fan clamp in the RCC slab as per IS 732 as required. |  | 75 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.011 | od120529/2024_2025 : Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374- 2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required.&lt;br&gt;&lt;br&gt; |  | 76 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.012 | 90.4.8 : Charges for cutting holes suitable for accommodating exhaust fans up to 305mm sweep including plastering colour washing etc. as required. |  | 33 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.013 | od120530/2024_2025 : Supply,conveyance, installation , testing and commissioning of 300/305 mm sweep Light Duty Exhaust fan in metal frame working on 230 V A/C in the existing opening, fixing necessary anchor bolts / bolt and nuts etc., as required including giving connections with the supplied wire along with the exhaust fan.&lt;br&gt;&lt;br&gt; |  | 33 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.014 | 90.15.4.3 : Supply Conveyance, installation, testing and commissioning of 70W LED street light output greater than 105lumen/W 4000-6000 K with IP 66 protection LED Chip make Cree/Lumilled/Nichea with power factor greater than 0.95 at full load, internal surge protection up to 8 KV,and Aluminium pressure die-cast Powder coated housing,acrylic cover complete with THD Less than 10%, power factor greater than 0.98, RoHS compliant, duly wired up for use on 230 V AC supply. Driver compartment should be seperatly accessible for maintenance (LM 79&80 certificates from NABL accredited Third party lab to be produced mentioning chip manufacturer) |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.015 | 90.15.3.3 : Supply installation testing and commissioning of Octogaonal Pole made of hot dip galvanised GI sheet 70 mm top diameter, 130 mm bottom diameter thickness 3mm base plate dimensions of 200x200x12 mm suitable for wind speed as per IS 875 Part III single arm bracket 0.5mt including connector foundation bolt 4 nos fixed in existing RCC foundation and junction box etc. complete 6 Meters |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.016 | 1.27.1 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.1 or 2 Module (75mmX75mm) |  | 32 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.017 | 1.27.2 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.3 Module (100mmX75mm) |  | 44 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.018 | 1.27.4 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.6 Module (200mmX75mm) |  | 33 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.019 | 1.24.1 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.5/6 amps switch |  | 76 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.02 | 1.24.3 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.15/16 amp switch |  | 34 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.021 | 1.24.4 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.3 pin 5/6 amp socket outlet |  | 76 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.022 | 1.24.5 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.6 pin 15/16 amp socket outlet |  | 50 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.023 | 90.10.3.14 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.024 | 90.10.3.33 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.025 | 90.10.3.32 : Supply and Fixing the following modular switches & accessories in the existing front plates and giving necessary connections as required (RoHS compliant ) |  | 16 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.026 | 1.21.1 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm |  | 2000 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.027 | 1.21.2 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.25 mm |  | 1500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.028 | 1.21.3 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.32 mm |  | 500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.029 | 1.17.3 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 X 1.5 sq.mm |  | 1500 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.03 | 1.17.12 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 2.5 sq. mm |  | 1000 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.031 | 1.17.21 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 4 sq. mm |  | 400 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.032 | 1.17.32 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.5 x 6 sq. mm |  | 800 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.033 | 90.6.4.55 : Supply and drawing 650/1100 V grade FRLS PVC insulated stranded single core copper conductor cables conforming to IS 694 part I 1990 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 600 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.034 | 90.6.5.11 : Supply and drawing the following sizes of multi-core PVC insulated & FRLS PVC sheathed 650/1100 V grade copper conductor round flexible cables conforming to IS 694 part I 1960 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.035 | 90.12.7.1 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.036 | 90.12.7.2 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.037 | 90.12.7.3 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.038 | 90.12.5.1 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.039 | 90.12.5.2 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.04 | 90.12.5.3 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 60 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.041 | od120545/2024_2025 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;2C X 4 Sq.mm Al Cable |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.042 | 9.1.1 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.2 X 6 sq. mm (19mm) |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.043 | 9.1.2 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.2 X 10 sq. mm (19mm) |  | 6 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.044 | 90.12.5.31 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in the existing RCC/ HUME / STONE WARE/ GI/ DWC pipe as required. |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.045 | 90.12.7.31 : Supply, laying and clamping of 1 no. PVC insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.046 | 9.1.24 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 95 sq. mm (45mm) |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.047 | 90.12.10.2 : Supply & laying of DWC pipe in ordinary soil 0.75m below ground level including excavation |  | 150 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.048 | 90.12.10.6 : Supply & laying of DWC pipe in ordinary soil 0.75m below ground level including excavation |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.049 | 90.16.1.1 : Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required |  | 130 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.05 | 90.16.1.2 : Supply and drawing bare earthing conductors of the following sizes along with wiring/ cables and giving connection as required |  | 60 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.051 | 90.16.5.1 : Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required. |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.052 | 90.16.5.2 : Supply of superior quality copper earth socket for the following size of earth conductor including crimping etc. as required. |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.053 | 2.3.4 : Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCBIRCCB/Isolator16 way, Double door |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.054 | 90.11.1.10 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.055 | 90.11.1.11 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 11 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.056 | 90.11.1.14 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.057 | 90.11.1.18 : Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.058 | 2.12.1 : Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.059 | 2.13.1 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.06 | 2.13.2 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.63 amps |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.061 | 2.13.3 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.100 amps |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.062 | 2.14.1 : Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.25 amps |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.063 | 2.15.2 : Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.064 | 2.10.1 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Single pole |  | 134 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.065 | 90.14.28.2 : S & F Motor starters of the following ratings |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.066 | 90.14.28.8 : S & F Motor starters of the following ratings |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.067 | 90.14.1.2 : Fabrication, supply, conveyance, installation testing and commissioning of floor or wall mounting, dust and vermin proof, cubicle type MV panel board comprising of the following components/ devices & complying to IS 8623.<br> Fabrication of fully partitioned, dust and vermin proof enclosure for panel assembly as per form 4 of IS 8623 (with latest amendments) using CRCA sheet as per approved design and requirement, with front and rear access facility, bus bar chambers, hinged doors for all switch gear compartments, earthing the doors using 4 sq mm braided copper conductor, providing necessary cut-outs for mounting meters, relays, indication lamps, bus bar interconnection etc, detachable covers for bus bar chamber and cable alley, powder coating the assembly after subjecting to 7 tank process etc as required. CRCA sheet alone be used for the fabrication. Angles/ flats/ slotted angles etc shall not be used for the fabrication of panel assembly. The measurments will be taken the area of the complete sheets used for panel board including partitions, folding, shrouding etc. |  | 14 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.068 | 90.14.2.1 : Supply and providing 2mm SMC sheet as shrouding for bus interconnection / terminations etc. including required nut & bolt etc. |  | 14 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.069 | 90.14.3.1 : Supply and providing heavy duty 'A' section neoprene gasket in the panel board |  | 26 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.07 | 90.14.4 : Supply and fabrication conveyance and installation of base frame of panel board using 75 x 40 mm rolled steel channel (ISMC) |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.071 | 90.14.5 : Supply and fabrication conveyance and installation of angle iron frame work for wall mounting panel board |  | 200 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.072 | 90.14.6 : Supply and providing copper bus bars including finger type SMC bus bar supports in the bus chamber, suitable size nut & bolt, providng heat shrink sleeves etc. as required. |  | 9800 | Cum cm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.073 | 90.14.7 : Supply and providing copper earth bus in the panel board |  | 4300 | Cum cm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.074 | 90.14.10.12 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.075 | 90.14.10.1 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 9 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.076 | 90.14.10.4 : Supply, conveyance and fixing the following types & current rated control gears & switchgears conforming to IS 13947 suitable for 440 V, 50 Hz, AC supply in the existing panel assembly as required. |  | 12 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.077 | od121591/2024_2025 : Supply and Fixing of Spreader Terminals for 4 pole MCCB in the existing panel board and giving connections etc. as required. 160A |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.078 | od121592/2024_2025 : Supply and Fixing of Spreader Terminals for 4 pole MCCB in the existing panel board and giving connections etc. as required.16A to 100A |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.079 | 90.14.11.2 : MCCB Accessories |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.08 | 90.14.11.11 : MCCB Accessories |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.081 | 90.14.11.9 : MCCB Accessories |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.082 | 90.14.11.13 : MCCB Accessories |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.083 | od120549/2024_2025 : Providing and fixing following multi function meter to read: V, A, F, 3 phase accuracy class 1 in existing panel and giving connection complete&lt;br&gt;&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.084 | od120550/2024_2025 : Supply and providing Red, Green, Black, Yellow, Orange colours LED indicators, AC/DC 22.5mm cut out dia&lt;br&gt;&lt;br&gt; |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.085 | od120551/2024_2025 : Supply and providing Blue Colour LED indicator lamp, AC/DC, 22.5 cm cut out dia&lt;br&gt;&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.086 | od121888/2024_2025 : Supply and fixing 20 A bake lite type HRC fuse base with 6A Fuse link in existing metal box and giving connections etc.as required.&lt;br&gt;&lt;br&gt; |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.087 | od121841/2024_2025 : Painting letters or figures of the following sizes with enamel paint as identification mark to SB, DB, panel board etc as required 2.50 cm, 4 cm or 5 cm height&lt;br&gt;&lt;br&gt; |  | 300 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.088 | 5.4 : Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.089 | od121805/2024_2025 : Supplying and laying 25 mm X 3 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt &amp; spring washer spaced at 50mm)&lt;br&gt;&lt;br&gt; |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.09 | 90.16.3.9 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.091 | 90.16.3.2 : Supply and clamping the following size of strips on surface of wall/ parapet/ existing cable tray using clamps fabricated from 20 X 3 mm GI flat duly painted or heavy duty GI spacer saddles spacing of clamps not exceeding 1 m, making good the damages, colour washing etc. as required ( for horizontal run) |  | 250 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.092 | 90.16.4.2 : Supply and clamping the following sizes of strips on surface of wall / parapet/ existing cable tray using clamps fabricated from 20 x3 mm GI flat duly painted or heavy duty GI spacer saddles, spacing of clamps not exceeding 1 m , making good the damages, colour washing etc. as required ( for vertical run). |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.093 | 6.14 : Providing and laying G.l. tape 32 mm X 6 mm from earth. electrode directly in ground as required. |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.094 | 6.3 : Fixing of lightning conductor finial (single prong) with base plate including holes etc. complete as required. |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.095 | 6.12 : Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.096 | od121229/2024_2025 : Supply and providing the following sizes of bolt and nut with washers on the existing MS box / earth bus etc. as required including drilling necessary holes as required.25 x 6 mm brass bolt &amp; nut&lt;br&gt;&lt;br&gt; |  | 30 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.097 | od121230/2024_2025 : Supply and providing the following sizes of bolt and nut with washers on the existing MS box / earth bus etc. as required including drilling necessary holes as required.25 x 3mm brass bolt &amp; nut&lt;br&gt;&lt;br&gt; |  | 30 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.098 | od121884/2024_2025 : supply and installation of dust and vermin proof , 3 phase syntax meter board(GS MB- 6535) and to fix KSEB meters, fuse units , CT etc as required including fixing it on wall, making good the damages colour washing etc. as required&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.099 | od121908/2024_2025 : Supply and providing 150/5A , 5VA resin cast metering CT with accuracy class 1 in the existing panel board and giving necessary connection as required- |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.1 | od121885/2024_2025 : Supplying and fixing 160, HRC Fuse Base with HRC Fuse link with connections, in existing meter board&lt;br&gt;&lt;br&gt; |  | 3 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.101 | od121886/2024_2025 : Supply and installation of 100 A, 2 Way neutral links mounted on DMC/SMC base&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.102 | od121890/2024_2025 : Supply and providing 9 Liter capacity GI Fire Bucket painted in post office red with primer coat of red oxide and written with white paint &apos;FIRE&apos; mounted on MS angle frame work/ wall bracket filled with fine sand, painting the bracket/ floor stand including making good the damages, colour washing etc. as required.&lt;br&gt;&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.103 | od121891/2024_2025 : Supply and providing First Aid Chart duly framed and placed in a conspicuous location for clear vision.&lt;br&gt;&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.104 | od121892/2024_2025 : Supply and providing 2.5mm thick Elastomeric fire retardant insulating mat as per IS 15652/2006 to withstand 11 KV dielectric strength.&lt;br&gt;&lt;br&gt; |  | 2 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.105 | od121893/2024_2025 : Supply and installation of Enamelled Danger Notice Board of size 200 x 150 mm. with inscriptions ( both in English and Malayalam) and conventional Skull and Bone in Red colour.&lt;br&gt;&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.106 | od121894/2024_2025 : Supply conveyance installation of portable type CO2 TYPE 4.5 KG Capacity fire extinguisher in position etc as required. |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.107 | od121895/2024_2025 : Supply conveyance installation of portable type ABC TYPE 5 KG Capacity fire extinguisher in position etc. as required&lt;br&gt;&lt;br&gt; |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.108 | od121823/2024_2025 : Preparation of the Drawing and Schematic diagram and obtain the Application form from the Electrical Inspectorate /KSEB the actual amount may be returned on produce of original Receipts.&lt;br&gt;&lt;br&gt; |  | 1 | Day |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.109 | od121824/2024_2025 : Charges for preparation of Electrical Schematic per A3 sheet first copy&lt;br&gt;&lt;br&gt; |  | 40 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.11 | od121825/2024_2025 : Copying charges for additional copies per A3 sheet&lt;br&gt;&lt;br&gt; |  | 75 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12 | SITC of 62.5 KVA DG Set | [7 empty] | 1
12.01 | od121231/2024_2025 : Supply &amp; Installation of 62.5 KVA Diesel Generator set and integral acoustic enclosure as per CPCB-1V norms and as per technical details given below. 1. Engine. a) Make of Engine - Leyland / Greaves / Kirloskar Green/Volvo Eicher b.Type of Engine - Diesel Engine. c. No. of Cylinders - As per manufactures standards. d. Method of cooling - Water cooled with radiator e. Aspiration - Turbo charged after cooled f. Design - Suitable for generating set operation. g. Out put -32 BHP at 1500 rpm under NTP condition,. 2. Standard accessories with Diesel Engine. a. Fly wheel to suit flexible coupling b. Close Coupling. c. Air cleaner. d. Radiator with fan provided with fan guard e. Fuel Pump. f. Mechanical governor. g. Fuel filter. h. Lubricating oil filter. i. Exhaust silencer. j. Exhaust Muffler k. Battery Charger/Generator 3. Engine Instrument Panel with the following items. a. Starting switch with key or button b. Lubricating oil pressure gauge. c. Water temperature gauge. d. RPM Indicator with hour meter. e. Battery charging ammeter. 4. Safety Controls for Engine a. Trip for low lubricating oil pressure. b. Trip for high water temperature. 5. Brushless Alternator a. Make - Stamford/ Crompton/Cummins/ Leroy Somer b. Type - Self exited and self regulated. c. Capacity - 25KVA/ 20kW @ 0.8 PF d. System of Voltage - 3 Phase, 415 V, 4 wire system e. Speed - 1500 rpm. f. Voltage regulation band - +/- 1% of rated voltage g. Frequency: 50 Hz h. Insulation - Class - H. The alternator should confirm to IS 4722. Operation and service manual, spares and tools shall be provided. 6. Fuel Tank Suitable size built in type integrated with the acoustic enclosure Fuel connection shall be done as per standards 7. Battery. Suitable capacity fully charged battery with leads and terminals of appropriate AH capacity as per Manufactures requirement. Automatic Battery charger. 8. Comprising of Gen-Set Controller-model KG934, which has indication / LCD displays available for Lube oil pressure, Battery voltage, Engine RPM, fuel level in the day tank, Engine Running hours, AC Current, AC Voltage, AC Frequency, AC Power metering with Safety trips for high engine temperature, low lube oil pressure, low radiator water level, low fuel level, under/over speed and high canopy temperature. The D.G set should have a warranty of three years. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.02 | od121256/2024_2025 : Supply and providing following size M. S. pipe - 5mm thickness complete with suitable size 12mm flange coupling with minimum 4/5mtr using allied packing with MS bolt with washer and rising the same on the wall/ parapet using chain pullies, scaffoldings, supports with M.S angles/channels etc. including painting the pipe with one coat of zinchromate primer over a coat of high temperature resistance alu. paint etc. for extending the exhaust pipe of the newly errected D. G. sets. 150/100 mm dia or nearest size B class MS pipe&lt;br&gt;&lt;br&gt; |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.03 | od121257/2024_2025 : Cladding for Exhaust system by wrapping mineral wool around the exhaust system (pipe) fixing it firmly with the pipe using chicken mesh applying overall coating to the system using 0.4mm thick aluminium sheet and make it air tight to ensure sound and thermal proof to the system&lt;br&gt;&lt;br&gt; |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.04 | od121252/2024_2025 : Supply and providing 12V,15A Automatic Battery charger suitable for 180Ah Battery, having . Full protection against battery overcharging &amp; reverse polarity. Over voltage, overload &amp; short circuit protection, reverse battery protection. Digital meters for voltage &amp; current display , Battery connecting terminals with lead wire, Float and Boost Charging Mode , LED Indication for charger status indication, etc: and giving necessary connections as required&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.05 | od121255/2024_2025 : Charges for conducting load test of 62.5 KVA DG set at standardised Factory bed as per standard norms and condition. ie in various steps load up to full load for 3 hours &amp; 10% over load for 20 minutes and the rate includes hire and rent of test bed equipment&apos;s, labour charges ,loading and unloading and fuel etc.The test certificate should be given the client in standard format&lt;br&gt;&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.06 | od121258/2024_2025 : Supply of High Speed Diesel for Load test and Trial Run&lt;br&gt;&lt;br&gt; |  | 100 | Litre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13 | SITC OF UPS | [7 empty] | 1
13.01 | od121851/2024_2025 : Supply &amp; installation of true online double - conversion DSP based 6.0KVA UPS system with 3 phases in and 3 phase out connecting in stand-alone configuration with indoor (IP20) with surge protection system, Input PF &gt;0.99, input THDi &lt;5 % without use of any external filters, double conversion technology with input voltage range 415 V @ full load, 50Hz Three Phase, output 415 V, 50Hz Three phase, It shall be 100% generator compatible, with Efficiency &gt; 93% and output power factor , Eco mode Efficiency 98% and including all accessories etc. as required. Offered UPS system with Type test certificates, and relevant IS standards. UPS shall be with automatic bypass built-in. The system shall have IGBT rectifier and inverter. Make: Eaton 9E-IN 6000VAXL 9E6KS-IN Online Double conversion pure sine wave output UPS system with 3 Year warranty |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14 | DATA | BI01010001010000000000000515BI0100001115 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14.01 | od124507/2023_2024 : Information Outlet RJ 45 - Supply, fixing, fluke testing and commissioning of CAT6 Information Outlets (Key stone) with Shuttered Faceplate, Single port, white, jack, suitable PVC / GI Modular Box etc. including necessary connections with all accessories required for complete installation as directed by the Engineer in charge. |  | 41 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.02 | od124508/2023_2024 : OFC Cable - Supplying and drawing of 6 core SM armoured Optical Fibre Cable (OFC) through wall / tray with all acessories as required for complete installation and as instructed by engineer in charge / consultant and making good all damages made for installation. |  | 151 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.03 | od124719/2023_2024 : CAT6 Cable - Supplying and drawing of Category 6 cable consists of 4 pairs of solid insulated copper 23AWG, surface / recessed medium class PVC conduit through wall / tray with all acessories as required for complete installation and as instructed by engineer in charge / consultant and making good all damages made for installation. &lt;br&gt; |  | 1417 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.04 | od124509/2023_2024 : Patch Cable - User Side - Supply, fixing, testing and commissioning of CAT6 Patch Cable - 2 Meter length etc. of approved make as required for complete installation. |  | 41 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.05 | od124510/2023_2024 : Patch Cable - Hub Side - Supply, fixing, testing and commissioning of CAT6 Patch Cable - 1 Meter of approved make as required for complete installation. |  | 41 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.06 | od124511/2023_2024 : Fibre Patch Cable - Hub Side - Supply, fixing, testing and commissioning of Fibre Patch Cable - 2 Meter of approved make as required for complete installation.&lt;br&gt; |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15 | Voice | [7 empty] | 1
15.01 | od124721/2023_2024 : Supply, installation, testing and commissioning of Basic user phone with necessary connection as required for complete installation as directed by the engineer in charge.&lt;br&gt; |  | 34 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.02 | od124722/2023_2024 : krone Box - Supply, erection, testing and commissioning of following pair krone with Box including mounting frame, enclosure of ISI grade with lockable front cover with all accessories required for for complete installation in wall as directed by the Engineer in charge.&lt;br&gt;50 Pair MDF Krone&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.03 | od124723/2023_2024 : krone Box - Supply, erection, testing and commissioning of following pair krone with Box including mounting frame, enclosure of ISI grade with lockable front cover with all accessories required for for complete installation in wall as directed by the Engineer in charge.&lt;br&gt;20 Pair&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.04 | od124724/2023_2024 : krone Box - Supply, erection, testing and commissioning of following pair krone with Box including mounting frame, enclosure of ISI grade with lockable front cover with all accessories required for for complete installation in wall as directed by the Engineer in charge.&lt;br&gt;10 Pair&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.05 | od124725/2023_2024 : Cable - Supplying and laying of following pair armoured telephone cable through wall/tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation. &lt;br&gt;50 Pair Telephone Cable&lt;br&gt; |  | 36 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.06 | od124726/2023_2024 : Cable - Supplying and laying of following pair armoured telephone cable through wall/tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation. &lt;br&gt;20 Pair Telephone Cable&lt;br&gt; |  | 92 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.07 | od124727/2023_2024 : Cable - Supplying and laying of following pair armoured telephone cable through wall/tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation. &lt;br&gt;10 Pair Telephone Cable&lt;br&gt; |  | 31 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.08 | od124737/2023_2024 : Cable - Supplying and laying of following pair armoured telephone cable through wall/tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation. &lt;br&gt;5 Pair Telephone Cable&lt;br&gt; |  | 18 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.09 | od124738/2023_2024 : Supply, Installation, Testing and Commissioning of &quot;PBX with 34 Analog extensions expandable up to 50 with maximum of 10 concurrent calls, 2 CO analouge trunk, IVR, Call Hunt etc. including 1 numbers master console phone &amp; short key / Direct Station Selection (DSS) Console&lt;br&gt;&quot;Built-In Auto Answer&lt;br&gt;Voice Mail Integration&lt;br&gt;Paging Announcement&lt;br&gt;Programmable Function Keys&quot;&quot;&lt;br&gt;Call Waiting&quot;&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.1 | od124739/2023_2024 : Surge Protection Device For EPABX: Supply, Installation, Testing and commissioning of SPD with enclosure, the surge protection device shall be suitable to protect telephone lines designed to with stand both lightning current and switching surges. Technology: GD tube, Nominal Voltage: 180 V, Pulsed Current (10/350 &micro;s ) Iimp: 1 KA, Nominal Discharge Current (8/20 &micro;s )/phase In: 5KA, Maximum discharge current: 10 KA,Voltage Protection Level(sym)&lt;700V, Response time&lt;1n sec&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.11 | od124728/2023_2024 : 2 Pair Cable - Supplying and drawing of 2 pair telephone cable consists of 0.5 mm dia FR, PVC Compound annealed copper conductor, unarmored telephone cable in surface / recessed medium class FRS PVC conduit through wall/tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation.&lt;br&gt; |  | 1198 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
15.12 | od124729/2023_2024 : Information Outlet RJ 11 - Supply, fixing, testing and commissioning of RJ11 Information Outlets (Key stone) with shuttered Faceplate, single port, white, jack, suitable PVC / GI Modular Box etc. including necessary connections with all accessories required for complete installation as directed by the Engineer in charge.&lt;br&gt; |  | 34 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16 | Closed Circuit Telivision (CCTV) | [7 empty] | 1
16.01 | od124743/2023_2024 : Network Video Recorder with Storage: Supply, installation, testing and commissioning of 32 Channel Network Video Recorder with Recording Storage space server for 30 days, Supports 32 channels 720 P resolution video recording at real time, NVR ONVIF supporting, Recording resolution of Max 4 MP, should support dual video HDMI output, H.265,H.264 at real time. Video storage expansion for recording, with all accessories required for complete installation and directed by engineer in charge. (Consider the sufficient HDDs for 720p @ 20 FPS for 30 days continues recording for all channels). Storage calculation details shall be submitted.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.02 | od124744/2023_2024 : LED Display - Supply, installation, testing and commissioning of 43 inch full HD LED display for video wall arrangement for 24 x 7 Setup including necessary connection, HDMI cable, rating tray etc. as required for complete installation with all accessories as required and directed by engineer in charge. &lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.03 | od124719/2023_2024 : CAT6 Cable - Supplying and drawing of Category 6 cable consists of 4 pairs of solid insulated copper 23AWG, surface / recessed medium class PVC conduit through wall / tray with all acessories as required for complete installation and as instructed by engineer in charge / consultant and making good all damages made for installation. &lt;br&gt; |  | 1301 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.04 | od124745/2023_2024 : Supply, installation, testing and commissioning of workstation with Intel I5 letest generation processror or above, 4 GB ram and 2 TB HDD with software for CCTV integration&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.05 | od124746/2023_2024 : Dome Camera - Wide - Supply, Installation, testing and commissioning of IP based 3.6 mm fixed lens, 2MP resolution, H.264 / H.265, 1/2.8&quot; Progressive Scan CMOS Day/Night, IR dome POE enabled camera, 20 to 30 meters IR range, 120 dB digital WDR with all connectors and necessary accessories for mounting in false ceiling as required for complete installation as directed by Engineer in charge.&lt;br&gt; |  | 23 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.06 | od124747/2023_2024 : Camera - Bullet - Supply, Installation,testing and commissioning of Varifocal Bullet Camera with 2 MP, H.264 / H.265, built-in IR LED, 2.8/3.6 mm to 9/12 mm, 20 to 30 meters IR range, IP 66 with all connectors and necessary accessories for mounting in false ceiling / True Ceiling as required for complete installation as directed by Engineer in charge. PoE (Power over Ethernet)&lt;br&gt; |  | 14 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
16.07 | od124776/2023_2024 : Network Video Recorder with Storage: Supply, installation, testing and commissioning of 16 Channel Network Video Recorder with Recording Storage space server for 30 days, Supports 16 channels 720 P resolution video recording at real time, NVR ONVIF supporting, Recording resolution of Max 4 MP, should support dual video HDMI output, H.265, H.264 at real time. Video storage expansion for recording, with all accessories required for complete installation and directed by engineer in charge. (Consider the sufficient HDDs for 720p @ 20 FPS for 30 days continues recording for all channels). Storage calculation details shall be submitted.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17 | Audio / Public Adressing System (PAS) | [7 empty] | 1
17.01 | od124779/2023_2024 : Wall Mounted Speaker - Supply, fixing, testing and commissioning of wall mounted Speakers with inbuilt line matching transformer with power 12W with a volume controller to adjust the volume individually as per the requirement with all accessories including wall mounting kit required for complete instllation. The volume controller shall be fixed separately as per the site condition for individual control. Cost inclusive of necessary interconnection including conduit, connection wire etc.&lt;br&gt; |  | 55 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.02 | od124780/2023_2024 : Mixing Amplifier - Supply, fixing, testing and commissioning of 240 Watts Mixer Amplifier with necessary jacks and cable for connections and interconnection with all accessories required for installation as required.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.03 | od124781/2023_2024 : Power Amplifier - Supply, fixing, testing and commissioning of Power Amplifier of 240 Watts with necessary jacks and cable for connections and interconnection with all accessories required for instllation as required.&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.04 | od124782/2023_2024 : Controller - Supply, fixing, testing and commissioning of Master zone controller with routing zone capcity of additional 6 zones with all acessories and necessary connections including necessary cables and jacks as required for complete installation. The work also include integration with Fire Alarm System (FAS) including to play the pre-recorded message in case of fire and evacuation.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.05 | od124783/2023_2024 : Call Stations - Supply, fixing, testing and commissioning of 6 Zone Calling Station with mic as per the drawing as required for complete installation.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.06 | od124784/2023_2024 : Audio/Video player - Supply, installation, testing &amp; commissioning of Audio/Video player with USB option with all accessories like jacks and codes for complete installation as required as directed by the Engineer in charge. &lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.07 | od124785/2023_2024 : Speaker Cable - Supplying and drawing of 2 Core, Twin Twisted, ATC tinned copper, overall sheathed, Armoured Speaker cable, 16 AWG for speakers through surface / Tray with all acessories as required for complete installation and as instructed by engineer in charge/consultant and making good all damages made for installation.&lt;br&gt; |  | 1265 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
17.08 | od124786/2023_2024 : Ceiling Mounted Speaker - Supply, fixing, testing and commissioning of ceiling mount Metal Grille Speakers with inbuilt line matching transformer with power 6W with all accessories required for complete instllation as required.&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18 | Active Components, Racks & Accessories | [7 empty] | 1
18.01 | od124798/2023_2024 : Supply, Installation, Testing and installation of Cat - 6, shuttered type, 24 port fully loaded patch panel with necessary cable manager for routing the cable inside rack with all accessories required for complete installation as required as directed by the engineer in charge.&lt;br&gt; |  | 5 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.02 | od124799/2023_2024 : Supply, Installation, Testing and installation of Cat - 6, 24 port 10/100/1000 Mbps, layer 2, POE, switch with rack mounting brackets, input connector shall be as per IEC-320-C14 with all accessories required for complete installation populated with minimum two numbers 1G SFP module for uplink and downlink and downlink as required as directed by the engineer in charge. The switch should be capable to provide suffient power budjet to IP cameras as per the requirement. |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.03 | od124800/2023_2024 : Supply, Installation, Testing and installation of 6 port Light Interface Unit (LIU) / Fibre Patch Panel, rack mountable with mounting brackets, loaded with Adapetors, Couplers Single Mode (SM) pigtails with splicing with all accessories required for complete installation as required as directed by the engineer in charge.&lt;br&gt; |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.04 | od124802/2023_2024 : Supply, installation, testing and commissioning of 9U Rack with Front glass door, Rear Perforated door with handle Lock &amp; key. Front / Rear 9U mounting angles, top, bottom open, RAL 9005 / 7035 texture finish, including necessary exhaust / circulation fan, 19&quot; Power Socket Strip with all accessories required for complete installation as directed by the engineer in charge.&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.05 | od124803/2023_2024 : Supply and fixing of UnPerforated Cable tray with cover / Ceiling Raceway closed with snap fit lid, suitable supports and brackets and other accessories as required confirming to IEC-61537. The Tray shall be galvanized for corrosion protection confirming to DIN EN 10346 / ISO 1461. The Ceiling Raceway shall be supplied with cover with the standard length of 3 Mtr.&lt;br&gt;50 mm width x 50mm Height with Cover &lt;br&gt; |  | 84 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.06 | od124804/2023_2024 : Supply and fixing of UnPerforated Cable tray with cover / Ceiling Raceway closed with snap fit lid, suitable supports and brackets and other accessories as required confirming to IEC-61537. The Tray shall be galvanized for corrosion protection confirming to DIN EN 10346 / ISO 1461. The Ceiling Raceway shall be supplied with cover with the standard length of 3 Mtr.&lt;br&gt;100 mm width X 50 mm depth X 1.6 mm thickness&lt;br&gt; |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.07 | od124885/2023_2024 : Supply, Installation, Testing and installation of Cat - 6, 16 port 10/100/1000 Mbps, layer 2, POE, switch with rack mounting brackets, input connector shall be as per IEC-320-C14 with all accessories required for complete installation populated with minimum two numbers 1G SFP module for uplink and downlink as required as directed by the engineer in charge. The switch should be capable to provide suffient power budget to IP cameras as per the requirement.&lt;br&gt; |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.08 | od124886/2023_2024 : Supply, Installation, Testing and installation of Cat - 6, 12 port 10/100/1000 Mbps, layer 2, POE, switch with rack mounting brackets, input connector shall be as per IEC-320-C14 with all accessories required for complete installation populated with minimum two numbers 1G SFP module for uplink and downlink as required as directed by the engineer in charge. The switch should be capable to provide suffient power budget to IP cameras as per the requirement.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.09 | od124887/2023_2024 : Supply, installation, testing and commissioing of 12U Rack with Front glass door, Rear Perforated door with handle Lock &amp; key. Front / Rear 12U mounting angles, top, bottom open, RAL 9005 / 7035 texture finish, including necesary exhaust / circulation fan, 19&quot; Power Socket Strip with all accessories required for complete installation as directed by the engineer in charge.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
18.1 | od124888/2023_2024 : Supply, installation, testing and commissioing of 21/22 U Rack DK_PS frame with Front glass door, Rear Perforated door with handle Lock &amp; key, castors. Side and rear panels, Front / Rear 42U 800Wx1000D MM mounting angles, top, bottom open, RAL 9005, including necessary exhaust / circulation fan with all other accessories required for complete installation as directed by the engineer in charge.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
19 | INVERTER SPLIT UNIT | [7 empty] | 1
19.01 | od124202/2023_2024 Supply, Installation, testing and commissioning of following capacity 5 star rated air cooled INVERTER, Ceiling /wall Mounted split type Air-conditioners each complete with scroll compressor, air cooled condensor, GSS casing, filters, cooling coils, fan motors, insulated copper refrigerant piping as per drawing, control wiring, refrigerant controls and accessories, including Micro- processor control with indication lamps for the operation of the system with thermostat fixed in the respective rooms to adjust the temperature according to the equipments with micro-processor control panel for each machine. Refrigerant shall be R410/R32. Price shall inclusive of all duties, installation, commissioning, Refrigerant piping upto a standard length of 3 meter and above 3 meter shall be measured separately. All Indoor Units shall be factory assembled, wired, piped and tested.<br>The indoor unit shall be with drain pump. Indoor units to be slim type, medium static units. Pre-filters to be part of all indoor units and all units shall be low db units. The indoor units should including the cordless remotes, refnet joints, control cabling between indoor & out door units, GI painted / powder coated frame works for outdoor units & making good of civil work's.<br>1.5 TR Hiwall Inverter Split Unit<br> |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
19.02 | od124203/2023_2024 Supply, Installation, testing and commissioning of following capacity 5 star rated air cooled INVERTER, Ceiling /wall Mounted split type Air-conditioners each complete with scroll compressor, air cooled condensor, GSS casing, filters, cooling coils, fan motors, insulated copper refrigerant piping as per drawing, control wiring, refrigerant controls and accessories, including Micro- processor control with indication lamps for the operation of the system with thermostat fixed in the respective rooms to adjust the temperature according to the equipments with micro-processor control panel for each machine. Refrigerant shall be R410/R32. Price shall inclusive of all duties, installation, commissioning, Refrigerant piping upto a standard length of 3 meter and above 3 meter shall be measured separately. All Indoor Units shall be factory assembled, wired, piped and tested.<br>The indoor unit shall be with drain pump. Indoor units to be slim type, medium static units. Pre-filters to be part of all indoor units and all units shall be low db units. The indoor units should including the cordless remotes, refnet joints, control cabling between indoor & out door units, GI painted / powder coated frame works for outdoor units & making good of civil work's.<br>1.0 TR Hiwall Inverter Split Unit<br> |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
20 | REFERIGERANT PIPING | [7 empty] | 1
20.01 | od124229/2023_2024 Supply, Installation, testing and commissioning of soft/hard drawn copper for liquid line / discharge line refrigerant piping of approved make for Invertor type split system, complete with necessary fittings, jointing / brazing including accessories, insulated with Class O closed cell nitrile rubber thermal insulation tube, having a density of 40-55 Kg/m3 with factory laminated 7 Mils glass cloth having UV protection. Thickness of the tube shall be 19 mm with a vapour diffussion resistance value of 7000 as per EN 12086 and thermal conductity of 0.035 @ 0 deg C mean temperature as per EN 12667 for Suction and Liquid lines. Adhesive should be from the same manufacturer, with all accessories required for complete installation as per specifications etc. as required.<br> |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
20.02 | od124230/2023_2024 Electrical Control Cabling: Supply, laying and termination of electrical control cum transmission cabling of suitable size and runs with FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit of suitable size between indoor and outdoor units.<br> |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
20.03 | od124231/2023_2024 Electrical Power Cabling: Supply, laying and termination of electrical power cabling of suitable size and runs including earth with FRLS PVC insulated copper conductor single core cable in PVC flexible conduit of suitable size from isloator to outdoor / indoor units outdoor units.<br> |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
20.04 | od124232/2023_2024 Drain Water Pipig: Supply, installation, testing and commissioning of condensate drain of PVC piping of adequate size (25 mm or above) as per BIS 4985 with necessary clamps, supports, hangers and fitting such as bend, tees, reducers, necessary traps etc. duly insulated with 9 mm thick closed cell nitrile rubber as per the drawing and technical specification.<br> |  | 35 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
20.05 | od124233/2023_2024 Perforated tray: Supply and fixing of Perforated tray with horizontal & vertical bends, reducers, Tee's, cross over, suitable supports and brackets and other accessories as required confirming to IEC-61537. The Tray shall be galvanized for corrosion protection confirming to DIN EN 10346 / ISO 1461. The trays should be tested for a max. safe working load of 150 Kgs with a span distance of 1.5 meters and the deflection should be within the limits as per standard. The safety factor shall be 1.7 times of the safe working load. The perforated tray shall be supplied with the standard length of 3 Mtr. Make: OBO Bettermann or Equivalent<br>50 mm width X 60mm Height<br> |  | 20 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
21 | FIRE HOSE REEL & HYDRANT SYSTEMS | BI01010001010000000000000515BI0100001116 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21.01 | od123169/2023_2024 : Supply, installation, testing and commissioning of Manual Swing Type Fire Hose Reel Complete Set with heavy duty drum / reel, 19 mm. dia, 30 Meter long 2-ply polyester yarn braided / rubber braided pressure hose, Red Coloured, heavy duty nylon on/off jet/spray nozzle, 22 mm. isolating valve and all other necessary fixing accessories including Fabrication and Erection of M.S. Support, as per requirement, for Fixing the Fire Hose Reel Set.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
21.02 | od123170/2023_2024 : Supply, installation, testing and commissioning of Fire Hydrant Valve, bearing to ISI:5290 Type-A mark, Stainless Steel-304 body with 63 mm. oblique instantaneous single outlet, 75 mm. N.B. flanged inlet, Stainless Steel - 304 spindle, complete with PVC blank cap, G.I. chain etc.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
21.03 | od123171/2023_2024 : Supply, installation, testing and commissioning of Fire Brigade Inlet Breeching, C.I. body, having 3 Way Gunmetal, 63mm. male instantaneous inlet, conforming to IS: 903, with non return valves, 25mm. drain valve, flanged outlet, 3 Nos. of rubber blank caps and G.I. chains. &lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
21.04 | od123172/2023_2024 : Supply, installation, testing and commissioning of Fire Hose, RRL hose jacketed with circular woven synthetic fiber. conforming to IS: 636:88, with Working Pressure 14 Kg/Cm2, Proof Pressure 22 Kg / Cm2 and Burst Pressure 38 Kg / Cm2. The Fire Hose shall be with IS: 636 Type-A marking and 63mm. dia., 15 Meter long with pair of 63mm. male and female instantaneous couplings, Stainless steel - 304, having IS: 903 mark and duly S. S. wire wounded. The hose shall be rolled and hung to suitable M. S. support in the Fire Hose Cabinet.&lt;br&gt; |  | 8 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
21.05 | od123173/2023_2024 : Supply, installation, testing and commissioning of Branch Pipe, Stainless Steel-304, short type, with 63mm. male instantaneous inlet, male threaded outlet, fitted with 16mm. bore nozzle, having IS: 903 mark.&lt;br&gt; |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
21.06 | od123174/2023_2024 : Supply and fix at site in position MS Fire Hose Cabinet made out of 16 gauge MS Sheet, wall / pole mounting type, to accommodate two 15m length of delivery hose and branch pipe, acrylic fronted double door, with lock, 2 keys and a break glass recess for keys, painted Fire Red. The words &quot;FIRE HOSE&quot; to be painted on the box. The price shall be inclusive of fixing with all accessories and as per requirement.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
21.07 | od124198/2023_2024 : Supply, installation, testing and commissioning of Fire Brigade Draw Off Outlet C.I. body, having 4 Way Gunmetal, 63mm. female instantaneous inlet, conforming to IS: 903, with non return valves, 25mm. drain valve, flanged outlet, 4 Nos. of rubber blank caps and G.I. chains. &lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
22 | AUTOMATIC FIRE SPRINKLER SYSTEM | [7 empty] | 1
22.01 | od123812/2023_2024 : Providing, fixing, testing and commissioning of Standard Coverage, Quick Response Automatic Fire Sprinkler, K- Factor: 5.6 (80 Metric) with all accessories necessary for complete installation. The Fire Sprinklers shall be UL listed / FM Approved&lt;br&gt;Pendant Type, 68 Degree C Rating. &lt;br&gt; |  | 189 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
22.02 | od124199/2023_2024 : Providing, fixing, testing and commissioning of Standard Coverage, Quick Response Automatic Fire Sprinkler, K- Factor: 5.6 (80 Metric) with all accessories necessary for complete installation. The Fire Sprinklers shall be UL listed / FM Approved&lt;br&gt;Upright Type, 68 Degree C Rating. &lt;br&gt; |  | 70 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
22.03 | od123814/2023_2024 : Providing &amp; Fixing 2 Piece Chrome Plated Friction Fit recessed escutcheon for pendant sprinklers, as per requirement. &lt;br&gt; |  | 70 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
22.04 | od123815/2023_2024 : Providing, Fixing, Testing and Commission Flexible Sprinkler Hose; UL Listed &amp; FM Approved, 25mm. (1&quot;) BSP Male Inlet, 15mm. (1/2&quot;) NPT Female Outlet, Braided, Working Pressure 13.8 Bar, 1 meter long, and with all connecting systems and accessories required for complete installation. &lt;br&gt; |  | 189 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
22.05 | od123816/2023_2024 : Providing, Fixing, testing and commissioning of Flow Switch, Vane type, IP 65 Protection with 20 Bar Working Pressure Protection with all necessary accessories, for monitoring Fire Sprinkler System. The control cabling from flow switches to Fire Sprinkler Annunciating Panel shall be measured separately.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23 | FIRE PUMPS AND ACCESSORIES | [7 empty] | 1
23.01 | od123982/2023_2024 : MAIN PUMP - Supply, installation, testing and commissioning of Horizontal long coupled End Suction Fire Hydrant Pump Set: Electrical Driven, Capacity: 1620 LPM at 55 Meter Head, conforming to IS 1520, with Bronze Impeller, S. S. Shaft, Mechanical Seal, High Efficient IE-3 rated, Squirrel Cage Induction Electric Motor, Suitable HP, 3Ph, 50 Hz, 2900/3000 RPM, TEFC, complete with necessary concrete foundation duly plastered, MS fabricated common base plate with foundation bolts, compound gauge, water re-circulation arrangement, pressure relief valve, anti-vibration mounts, as per requirement and nececssary earthing of Electric Motors, etc. all as per the Technical Specifications, Prevailing Rules, Standards, Requirement and Site Conditions.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.02 | od123984/2023_2024 : JOCKEY PUMP - Supply, installation, testing and commissioning of Jockey Pump: Electrical Driven, Capacity: 180 LPM at 60 Mtrs. Head, Vertical Multi Stage Inline Pump with S.S Impeller, Mechanical Seal, and with High Efficient IE-3 Rated Squirrel Gauge Induction Motor, Suitable HP, 3Ph, 50 Hz, 2900/3000 RPM, TEFC, complete with necessary concrete foundation duly plastered, MS fabricated common base plate with foundation bolts, compound gauge, water re-circulation arrangement, pressure relief valve, anti-vibration mounts, as per requirement and nececssary earthing of Electric Motors, etc. all as per the Technical Specifications, Prevailing Rules, Standards, Requirement and Site Conditions.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.03 | od123985/2023_2024 : DIESEL PUMP - Supply, installation, testing and commissioning of Stand By / Back Up Fire Pump, Horizontal long coupled, End Suction Pump, Engine Driven, suitable for Automatic operation and consisting of the following and complete in all respect as required; Capacity: 1620 LPM at 55 Meter Head conforming to IS 1520, with Bronze Impeller, S. S. Shaft, Mechanical Seal, coupled to High Efficient Radiator Cooled Diesel Engine, Suitable HP, 2150/2920 RPM, and with Control Panel with Auto Starting Facility, by activation of concerned Pressure Switch and thro. 12V/24 V Electric Starter, Battery of adequate rating and with Battery Charger, Battery Leads, Diesel Tank for 6 hrs operation, exhaust pipe extended up to 1 mtr outside pump house, duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per specification, complete with necessary civil foundation, foundation bolts, compound gauge, water re-circulation arrangement, pressure relief valve, and all other necessary fixing accessories, all as per Technical Specifications.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.04 | od123986/2023_2024 : Supply, erection, commissioning of additional length of Exhaust Pipes with long radius bend from silencer with necessary clamps, fixtures, civil works andthermal insulation with 50 mm thick glass wool and with 1.0 mm thick aluminium sheet cladding of following adequate size including suitable rain cap for top to avoid rain water entry. The distance between exhaust pipe at top and rain cap should be higher than diameter of pipe. The horizontal run of exhaust piping should slope downwards away from engine to the condensate trap. Silencer should be installed with drain plug at bottom. Fixing shall be done with proper clamps, expansion bolts, and all other acessories as instructed by the Engineer and the rate inclusive of all minor civil works required, bolts, clamps etc as required for istallation. Support to exhaust piping should be done in such a manner that load of exhaust piping is not exerted to turbocharger. Exhaust pipe height shall be 3m more than the top of any adjacent building withing 10m radius of the exhaust.&lt;br&gt; |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.05 | od123987/2023_2024 : MOTOR CONTROL PANEL - Fabrication, supply, erection, testing and commissioning of cubicle type, dust and vermin proof, floor mounted, front operated Common Control Panels for Main Fire Pumps &amp; Jockey Pumps, made out of 16 SWG thick CRCA sheet fully compartmentalised complete with hinged and earthed front doors with name plate, danger notice board, heavy duty rubber gaskets, removable gland plates (top entry) made out of 3mm thick sheet steel including all components as shown in the schematic drawing. All opening parts of the panel shall be sealable. The panel shall be IP: 54 protection, complete with Main Isolator, Bus Bar Chamber, Volt Meter, Ammeter, Individual Star- Dealt Starters for Main &amp; Sprinkler Pumps, DOL Starter for Jockey Pumps, Contactors, Auxiliary Contacts, Timers for automatic operation and to avoid freequent re-starts, Indicating Lamps, Fuses, Auto / Manual Selector Switches for all Fire Pumps, Manual On / Off Buttons for Jockey Pump &amp; Manual On Buttons for Main Pumps, all internal wiring etc. The price for Control Panel shall be inclusive of, Control Cabling, in Steel Conduits, for automatic starting of Main Pumps &amp; Automatic start and stop for Jockey Pump and Earthing of the Panel, all as per Technical Specifications, Schematic Drawing, Prevailing Rules, Standards, Requirement and Site Conditions. The Panel shall be to the approval of Kerala State Electrical Inspectorate.&lt;br&gt;Incomer - 125A, FP, MCCB Isolator - 1No.&lt;br&gt;125A, 415V, 25 kA best conductivity Al TPN bus bar with SMC supports, heat shrinkable sleeves etc complete as required. &lt;br&gt;Multi function digital LED meters with accuracy class 1, with necessary CT and accessories for measuring Voltage, current, Frequency, Power Factor, kW, kVA, Old energy, On hours, site selectable kWh/kVAh&lt;br&gt;Class B + C / Class 1 + 2 Surge arrestor device with necessary MCCB for protection of same - 1 Set.&lt;br&gt;RYB phase indicating LED lamps with control fuses and switches - 1 set.&lt;br&gt;Outgoing&lt;br&gt;63 A, TP+NL, MCCB Isolator + Star delta starter with all accessories Without overload relays / protection - 1 Set.&lt;br&gt;32A, TP+NL, MCCB Isolator + DOL Starter with all accessories with overload realy and single phase preventor - 1 Set.&lt;br&gt;&quot;25A, DP Isolator for diesel engine battery charger - PLC Control for Diesel Engine comprising:-&lt;br&gt;(i) Auto/Manual selector switch &amp; 3 attempt starting device, timers and relays as required, push buttons, start/stop in manual mode.&lt;br&gt;(ii)Indication lamp for High/Low Lub. Oil pressure, High Water Temp. and Engine ON indication.&lt;br&gt;(iii)SMF Battery VRLA type with charger suitable for 12 V/ 24 V DC with boost and tickle selector switch, 0-30 V DC volt meter, 0-20A DC Ammeter.&lt;br&gt;(iv)All standard relays and accessories for automatic operation of diesel engine.&lt;br&gt;e) All automatic operation of Main Pump, Sprinkler Pump &amp; Jockey Pump as per IS/CPWD specification &quot;&lt;br&gt;Supply, Installation, Testing &amp; Commissioning&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.06 | od123988/2023_2024 : Supply, installation, testing and commissioning of Pressure Switches with pressure rating suitable for above Fire Pumps, with a differential of 0.2 to 1.6 Bar, as per Technical Specifications.&lt;br&gt; |  | 3 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
23.07 | od123989/2023_2024 : Supply, installation, testing and commissioning of Diaphragm Pressure Vessel, 112 Ltrs Capacity, 15 Bar Working Pressure at a maximum flow rate of 2850 LPM. The vessel shall be with replaceable interior air cell, metallic outer shell, base, air release valve etc, all as per Technical Specifications.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24 | FIRE PIPES, VALVES & ACCESSORIES | [7 empty] | 1
24.01 | od123851/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;150mm |  | 18 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.02 | od124200/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Fire Line Pipe Work with Heavy Duty (Class-C) Galvanized Steel Pipes, confirming to IS: 3589/1239 Part - I. The pipe with Heavy Duty Galvanized Ductile Iron Screwed Fittings for Pipes up to 50 mm diameter. The pipe with Galvanized Grooved Fittings for pipes above 50mm diameter. The pipe with But Welded fittings for pump room for all sizes. Piping shall be with all accessories required for complete installation such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, grooving, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports, as per requirement, providing higher sizes of Sleeves/Opening, wherever required, and closing the gap between the pipes and sleeves/openings with 2 Hr. Fire Rated compound / sealant to the approval of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification. All Pipe Fittings shall be UL Listed and FM Approved, as per the technical specification.&lt;br&gt;25 mm.&lt;br&gt; |  | 378 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.03 | od124201/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Fire Line Pipe Work with Heavy Duty (Class-C) Galvanized Steel Pipes, confirming to IS: 3589/1239 Part - I. The pipe with Heavy Duty Galvanized Ductile Iron Screwed Fittings for Pipes up to 50 mm diameter. The pipe with Galvanized Grooved Fittings for pipes above 50mm diameter. The pipe with But Welded fittings for pump room for all sizes. Piping shall be with all accessories required for complete installation such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, grooving, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports, as per requirement, providing higher sizes of Sleeves/Opening, wherever required, and closing the gap between the pipes and sleeves/openings with 2 Hr. Fire Rated compound / sealant to the approval of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification. All Pipe Fittings shall be UL Listed and FM Approved, as per the technical specification.&lt;br&gt;200 mm.&lt;br&gt; |  | 8 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.04 | od123852/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;100mm |  | 39 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.05 | od123853/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.80mm |  | 58 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.06 | od123854/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;50mm |  | 128 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.07 | od123855/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;65 mm.&lt;br&gt; |  | 68 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.08 | od123857/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;40 mm.&lt;br&gt; |  | 97 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.09 | od123858/2023_2024 : Hydrant, Sprinkler System &amp; Plant Room : Providing, fixing, pressure testing and commissioning of Above Ground Pipe Work with Heavy Duty (Class-C) Mild Steel Pipes, confirming to IS: 3589/1239 Part - I (wherever applicable) and with Heavy Duty Black Ductile Iron Screwed Fittings for Pipes up to 50mm. dia. and But Welded Fittings, for pipes above 50mm. dia. confirming to IS:1239 Part - II with all accessories such as tees, elbows, reducers, check nuts, unions, flanges, nipples and neoprene gasket, bolts, nuts, washers etc. including cutting, threading, welding, joining, fixing in ducts, on walls, ceiling etc. by using suitable and strong enough supports as per requirement, providing higher sizes of Sleeves / Opening, wherever required, and closing the gap between the pipes and sleeves/openingsas per the direction of Engineer - in - Charge /Consultant. The total pipe work shall be protected with approved painting system as per technical specification.&lt;br&gt;32 mm.&lt;br&gt; |  | 69 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.1 | od123874/2023_2024 : Providing, fixing, testing and commissioning of Forged Ball Valve, PN-16 or above gunmetal /cast alloy, SS handle including necessary accessories and connections.&lt;br&gt;25 mm.&lt;br&gt; |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.11 | od123875/2023_2024 : Providing, fixing, testing and commissioning of Forged Ball Valve, PN-16 or above gunmetal /cast alloy, SS handle including necessary accessories and connections.&lt;br&gt;50mm&lt;br&gt; |  | 1 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.12 | od124433/2023_2024 : Providing, fixing, testing and commissioning of Butterfly Valve, PN-16 or above, slim seal, standard lever operated type confirming to BS:5155 with IS: 13095 Mark, with required companion flanges, nuts, bolts etc. complete. &lt;br&gt;200 mm.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.13 | od124434/2023_2024 : Providing, fixing, testing and commissioning of Butterfly Valve, PN-16 or above, slim seal, standard lever operated type confirming to BS:5155 with IS: 13095 Mark, with required companion flanges, nuts, bolts etc. complete. &lt;br&gt;100 mm.&lt;br&gt; |  | 16 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.14 | od124435/2023_2024 : Providing, fixing, testing and commissioning of Butterfly Valve, PN-16 or above, slim seal, standard lever operated type confirming to BS:5155 with IS: 13095 Mark, with required companion flanges, nuts, bolts etc. complete. &lt;br&gt;80 mm.&lt;br&gt; |  | 3 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.15 | od123941/2023_2024 : Providing, fixing, testing and commissioning of Non Return Valve, Wafer Swing Check type, PN-16 or above, Vertical / Horizontal Type , as per final requirement, conforming to IS: 13095 with nuts, bolts etc. complete. &lt;br&gt;80 mm. &lt;br&gt; |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.16 | od123942/2023_2024 : Providing, fixing, testing and commissioning of Non Return Valve, Wafer Swing Check type, PN-16 or above, Vertical / Horizontal Type , as per final requirement, conforming to IS: 13095 with nuts, bolts etc. complete. &lt;br&gt;100mm |  | 2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.17 | od123975/2023_2024 : Supply, installation, testing and commissioning of following 4&quot; dia. Bourdon Type Pressure Gauge, with ISI Mark or of equivalent International Standards.&lt;br&gt;Standard Type for indoor use Pressure Gauge with shut off cock and connection Pipe&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.18 | od123976/2023_2024 : Supply, installation, testing and commissioning of following 4&quot; dia. Bourdon Type Pressure Gauge, with ISI Mark or of equivalent International Standards.&lt;br&gt;Weather / Water Proof Type Pressure Gauge with shut off cock and connection Pipe&lt;br&gt; |  | 6 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.19 | od123977/2023_2024 : Providing and fixing sight glass assembly of brass body and brass ball with chrome plated Test &amp; drain valave, steel handle, PN16 or above, UL Listed &amp; FM Approved. Test and drain valve shall be with compact 3 position ball valves with drain orifice having K-factor 5.6 and a sight glass. 3 positions consist of OFF, TEST and DRAIN. Test and drain valves shall be provided for test as well as express drain functions in wet sprinkler systems with grooved end connection ends. The Test and Drain Valve shall be in Brass ASTM B584 material of construction. These have integral tamper resistant sight glass.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.2 | od123978/2023_2024 : Supply, installation, testing and commissioning of Hydraulically Operated Fire Sprinkler Alarm Valve (Installation Control Valve), Grooved End, UL Listed / FM approved, complete with Constant Pressure Trim Assembly, Water Motor Gong, control valves, pressure switch, pressure gauges etc. including all necessary fixing accessories. &lt;br&gt;150mm. Size&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.21 | od124275/2023_2024 : Supply, installation, testing and commissioning of Air Release Valve Gunmetal, conforming to IS 903:1993, having rubber ball with sealing seat and with 25mm. BSP threaded male inlet, including necessary accessories and connections.&lt;br&gt; |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
24.22 | od124276/2023_2024 : Providing, fixing, testing and commissioning of Non Return Valve, Wafer Swing Check type, PN-16 or above, Vertical / Horizontal Type , as per final requirement, conforming to IS: 13095 with nuts, bolts etc. complete. &lt;br&gt;150 mm.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25 | INTELLIGENT ADDRESSABLE FIRE ALARM SYSTEM | [7 empty] | 1
25.01 | od124288/2023_2024 : Supply, install, test and commission of microprocessor based, Intelligent Addressable, true Peer-to-Peer networkable, Fire Alarm Control Panel (MCP) as per the technical specification and to having a Visual Touch Screen Display Unit with Battery Back up for 24 hours for normal operation and 1 hours on alarm condition. The control panel, battery charger etc, shall be UL listed approved. The panel shall networked together and capable of networking with other compatible panels and compactible for BMS connectivity (Backnet/Modbus). The Panel shall have sufficient Loop Capacity to accomodate the devices and detectors as per the final design for this project with 10 % spare capacity in each loop. The panel shall be expandable for future upgradation, all as per Technical Specifications. &lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.02 | od124289/2023_2024 : Supplying, installation, testing &amp; commissioning of intelligent analog addressable Photothermal detector complete with mounting base complete as required&lt;br&gt; |  | 96 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.03 | od124290/2023_2024 : Supplying, installation, testing &amp; commissioning of intelligent analog addressable Photothermal detector complete with mounting base complete as required - Above ceiling&lt;br&gt; |  | 39 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.04 | od124291/2023_2024 : Supplying, installation, testing &amp; commissioning of intelligent addressable thermal detector with rate of rise cum fixed tempreature thermistor complete with base as required.&lt;br&gt; |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.05 | od124292/2023_2024 : Supplying, installation, testing &amp; commissioning of addressable manual call point complete as required.&lt;br&gt; |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.06 | od124293/2023_2024 : Supplying, installation, testing &amp; commissioning of addressable horn cum strobe complete as required.&lt;br&gt; |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.07 | od124294/2023_2024 : Providing, fixing, testing and commission Intelligent Addressable Input / Monitor Module, as per specification for interface with Flow Switches, Fire Pumps, Supervisory Switches, Alarm Valve, Water Tank Level etc.&lt;br&gt; |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.08 | od124295/2023_2024 : Supplying, installation, testing &amp; commissioning of addressable fire control module complete as required.&lt;br&gt; |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.09 | od124296/2023_2024 : Supplying, installation, testing &amp; commissioning of fault isolator complete with base as required.&lt;br&gt; |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
25.1 | od124297/2023_2024 : Supplying &amp; laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring &amp; LSZH outer sheath complete as required.&lt;br&gt; |  | 1019 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
26 | FIRE EXTINGUISHERS | [7 empty] | 1
26.01 | od124416/2023_2024 : Providing, fixing, commission and install in position following Portable Fire Extinguisher as per BIS 2190 and BIS: 15683:2006 and with relevant ISI Stamping/Marking.&lt;br&gt;ABC Dry Powder, Propellant - Dry Nitrogen, Store Pressure Type - 4 Kg. &lt;br&gt; |  | 15 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
26.02 | od124417/2023_2024 : Providing, fixing, commission and install in position following Portable Fire Extinguisher as per BIS 2190 and BIS: 15683:2006 and with relevant ISI Stamping/Marking.CO2 - 4.5Kg.&lt;br&gt;&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
26.03 | od124418/2023_2024 : Fire Bucket including Fabricated M. S. Stand&lt;br&gt; |  | 6 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
27 | TALK BACK SYSTEM | [7 empty] | 1
27.01 | od124438/2023_2024 : &quot;Supply, installation, testing &amp; commisioning of micro process based automatic talk back system with controller of 18 Zone, 500 W amplifier, Goose neck type microphone, complete with floor to floor announcing and talk back facilities with the following features and made functional: (a) Feather type key pads to select the zones. (b) Moulded plastic attractive enclosure. (c) Backlight Liquid Crystal Display (LCD) (d) User friendly interactive display. (e) Announcement selector - PH Switch. (f) Listen selector switch. (g) All Call switch to select all zones simultaneously for announcement (h) Zones Call Display On the LCD With Audio Alarm.&lt;br&gt;Controller Unit with 500 W amplifier, Goose neck type microphone and with the following features: (i) Built in Power supply. (ii) Zone Selector switching Circuit (iii)Terminal blocks to terminate zones wires, amplifier wires etc., (iv) Zone Call processing Circuit etc and made functional. Panel to be installed in the Fire Control Room.&quot;&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
27.02 | od124439/2023_2024 : Supply, installation, testing and commisioning of Public Address speaker with talk back facility 6 Watts with L M T and call switch, made out of powder coated CRCA sheet, wall mounting type and to be installed at a height of not less than 150 CM from the finished floor levels, suitable for concealed mounting.&lt;br&gt; |  | 7 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
27.03 | od124440/2023_2024 : Providing, fixing / laying, test and commission 2Core x 1.5 mm2 FRLS Armored Cables with Red Colour / Finish, as per Technical Specifications.&lt;br&gt; |  | 293 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
28 | SIGNAGES | [7 empty] | 1
28.01 | od124457/2023_2024 : Fire Exit Light - Laser type, with High Glow LED Light, size: 12&rdquo; x 6&rdquo; or nearby, Ceiling Mounting type with hanging clamps, on/off switch, Red / Green Colour option, power consumption: 8 Watt or less with all accessories required for complete installation as directed by the engineer inc charge. Power supply shaould be provided with UPS back-up.&lt;br&gt; |  | 10 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
28.02 | od124458/2023_2024 : Floor Identification Signage ( ie, GROUND FLOOR, FIRST FLOOR, etc.) at each stair enclosure on every floor, indicating the floor number in words, lettering size shall be 5 Cm. with contrasting colour from back ground. Size shall be 15cm x 30cm.&lt;br&gt; |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
28.03 | od124459/2023_2024 : Floor Identification Signage (MAIN STAIRCASE, FIRE STAIRCASE, FIRE ASSEMBLY POINT, PUMP ROOM, FIRE CONTROL ROOM, ELECTRICAL ROOM, FIRE LIFT, PASSENGER LIFT Etc.) at each stair enclosure on every floor, indicating the floor number in words, lettering size shall be 5 Cm. with contrasting colour from back ground. Size shall be 15cm x 30cm.&lt;br&gt; |  | 18 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
28.04 | od124460/2023_2024 : Supply and install in position the Signage &quot;FIRE ORDER&quot; it should contain the matter specified in the technical details on 3mm thick &quot;Opaque&quot; PVC foam board of computerized cut, PVC non-reflective self adhesive vinyl painted foam board of 2&apos; x 3&apos;.&lt;br&gt; |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
28.05 | od124486/2023_2024 : Supply and install in position following Sign Boards made out of 3mm thick &quot;Opaque&quot; PVC foam board with computer cut, PVC non-reflective self adhesive vinyl painted foam board, complete with mirror fasteners with all accessories required for complete installation as directed by the Engieer in charge.&lt;br&gt;-Signage Printed &quot;IN CASE OF FIRE, USE STAIRS UNLESS INSTRUCTED OTHERWISE&quot; of 1.25cm. height letters in red with white back ground. The size of the board shall be 25 x 30 Cm. and shall be fixed at the height of 2Mts. from finished floor near Manual Pull Stations.&lt;br&gt; |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
29 | MISCELLANEOUS ITEMS | [7 empty] | 1
29.01 | od124492/2023_2024 : Fabrication, supply, installation at site Heavy Duty Galvanized Mild Steel Puddle Flange, Fabricated from Heavy Grade M. S. Pipe, confirming to IS: 1239/ 3589, with PN:20 Drilled M.S. Flange(s), as per Table BS-10 and M.S. Plate, all as per tender drawings and technical specifications, provided. After total fabrication, the puddle flange should be hot dipped galvanized to IS: 4759 and further protected with Epoxy Coating to the approval of the Engineer - in - charge and Consultant.&lt;br&gt;200 mm dia&lt;br&gt; |  | 2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
29.02 | od124493/2023_2024 : Fabrication, supply, installation at site Heavy Duty Galvanized Mild Steel Puddle Flange, Fabricated from Heavy Grade M. S. Pipe, confirming to IS: 1239/ 3589, with PN:20 Drilled M.S. Flange(s), as per Table BS-10 and M.S. Plate, all as per tender drawings and technical specifications, provided. After total fabrication, the puddle flange should be hot dipped galvanized to IS: 4759 and further protected with Epoxy Coating to the approval of the Engineer - in - charge and Consultant.&lt;br&gt;100 mm dia&lt;br&gt; |  | 1 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30 | STP Electromechanical Works | BI01010001010000000000000515BI0100001117 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30.01 | od120045/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of NaOCl Dosing Tank - Pre &amp; Post with Capacity : 50 Litres&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30.02 | od120047/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Flocculant Dosing Tank with Capacity : 50 Litres&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
30.03 | od120048/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Coagulant dosing tank with Capacity : 50 Litres |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.04 | od120049/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Dewatering flocculant - sludge treatment Diaphragm Type with Electro-magnetic Power Unit, Single Phase |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.05 | od120050/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Hypochlorite Dosing Pump, Diaphragm Type with Electro-magnetic Power Unit, Single Phase |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.06 | od120051/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of dosing pumps Flocculant &amp; Coagulant Dosing Pump, Diaphragm Type with Electro-magnetic Power Unit, Singl Phase with design capacity 0-4 lph @ 5.5 Bar , 0.5 hp |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.07 | od120052/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of IR Pumps Progressive Cavity pumps, 5.0 m3/hr @ 10 m head; MOC -Stator CI rubber lined, Rotor SS, coupled with 1 HP, 3 Phase motor with design capacity of 2.7 m3/h, Head @10m |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.08 | od120054/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Filter Feed Pumps; End suction centrifugal surface mounted with CI Casing &amp; Impeller and SS Shaft. 1.92 m3/hr @ 35 m head coupled with 1.5 HP, 3 Ph motor 0.91 m3/hr @ 35 m head |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.09 | od120055/2024_2025 : Design,Supply,Installation,Testing &amp; Commissioning of Sludge Transfer Pumps; Submersible Centrifugal type, Open Impeller Type. 6.0 m3/hr @ 12 m head Solids handling capacity: 35 mm. Casing &amp; Impeller MOC: CI; Shaft Stainless Steel. Pump coupled with 1 HP, 3 Ph Submersible motor with design capacity 0.07 m3/h, Head @10m. |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.1 | od120056/2024_2025 : Design,Supply,installation ,Testing &amp; Commissioning of Raw Sewage Transfer pump, submersible, centrifugal type with cutter impeller and other accessories: 4 m3/hr @ 10 m head. Solids handling capacity: 35 mm. Casing &amp; Impeller MOC: CI; Shaft Stainless Steel. Pump coupled with 1 HP, 3 Ph submersible motor 0.84 m3/hr @ 10 m head |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.11 | od120058/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Electromagnetic flow meter with current flow reading and totalizer&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.12 | od120060/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Pressure gauges-diaphragm, for water line&lt;br&gt; |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.13 | od120061/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Pressure gauges-bourdon, for air line&lt;br&gt; |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.14 | od120062/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Level switches with suitable length of cable as per the site conditions for equalization, sludge, filter feed, UF Feed, Treated Water Tanks&lt;br&gt; |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.15 | od120063/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Control Panel, Form 2, with ON/OFF/AUTO modes for all pumps, blowers etc. provided with all necessary controls for proper operation of STP&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.16 | od120064/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Tubesettler Media, PVC&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.17 | od120065/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of MBBR Tank Sieves, Stainless Steel SS 304&lt;br&gt; |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.18 | od120066/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Proven Bio-Media, MOC Virgin HDPE, with specific gravity 0.95, protected surface area of 800 m2/m3 , with average diameter of the bio-media 25 mm and the internal wall thickness of 0.2 to 0.3 mm and outer wall thickness of 0.3 to 0.4 mm, to ensure optimum biofilm growth consistently.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.19 | od120067/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Maintenance-free Aeration grid for MBBR tanks, MOC: uPVC&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.2 | od120068/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Mixers with gear motor for anoxic, coagulation and flocculation tanks. Mixing paddle fabricated locally and coupled with slow speed gear motor drive.&lt;br&gt; |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.21 | od120069/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Coarse Screen, MOC SS 316 installed in Coarse Screen Channel&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.22 | od120070/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Sludge Dewatering System, Bag Filtration type, 2 Bag Filtering unit with MOC of all wetted parts and housing in SS 304, supplied with 25 Nos. sludge filter bags (washable-reuseable for a certain number of times)&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.23 | od120071/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Ultrafiltration System, Skid-mounted, Complete system including feed pumps, CIP System with pump, dosing system, interconnecting pipes, valves, control system etc.&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.24 | od120072/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Activated Carbon media (IV 1050) for ACF&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.25 | od120073/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Multigrade Sand media for PSF&lt;br&gt; |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.26 | od120074/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Filter vessels for PSF and ACF, MOC FRP, 400 dia x 1650 height with multiport valve for annual operation&lt;br&gt; |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.27 | od120075/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Air Blowers, Positive Displacement, Lobe Type, Capcity 75 Nm3/hr @ 0.35 kg/cm2, couple with 5 HP, 3 Ph, Motor. |  | 2 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
30.28 | od120076/2024_2025 : Design,Supply,Installation ,Testing &amp; Commissioning of Dewatering Dosing Tank |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information