## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: WAPCOS Limited
Work Name : Development of District Hospital at Chengannur, Alappuzha District - MGPS
Contract No: WAP/INFRA/KERALA/2024/CMGP/494-1
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Oxygen Supply System | BI01010001010000000000000515BI0100001113 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | od250758/2022_2023 : Fully Automatic Main Oxygen supply system with manifold : Supply, Installation, testing and commissioning of Fully automatic gas control panel with flow capacity of 1500LPM at 5 bar regulating/Supply presuure. Should have the connectivity of the Cylinder service and liquid oxtgen plant. suitable for Manifold capacity - 2 x 10 cylinder capacity (As per technical specification Standard: ISO 7396 -1 / HTM 02-01) |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | od250761/2022_2023 : Supply, Installation, Testing and commissioning of Oxygen Manifolds - 2 banks x 10 cylinders with tail pipes, NRV, fixing chain etc. The installation must fully comply with the standard ISO 7396/HTM 02-01 Please check technical specifications for complete details.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | od250762/2022_2023 : Supply, Installation, Testing and commissioning of Oxygen Manifolds - 2 banks x 4 cylinders with tail pipes, NRV, fixing chain etc. The installation must fully comply with the standard ISO 7396/HTM 02-01 Please check technical specifications for complete details.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | Nitrous Oxide Supply System | [7 empty] | 1
2.01 | od250763/2022_2023 : Supply, Installation, Testing and commissioning of fully automatic control panel N2O with Nominal flow rate of 300 LPM suitable for 2x4 cylinder manifold . The installation must fully comply with the standard ISO7396-1 or Equivalent. Please check technical specifications for complete details |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.02 | od124139/2024_2025 : Supply, Installation, Testing and commissioning of Emergency Cylinder Manifold 2 bank x 2 cylinders with emergency N2O high flow regulator with gauges and safety valves and tail pipes, NRV, fixing chain etc. The installation must fully comply with the standard ISO 7396/HTM 02-01. Please check technical specifications for complete details. |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | od124140/2024_2025 : Supply, Installation, Testing and commissioning of N2O Manifold - 2 banks x4cylinders with with tail pipes, NRV, fixing chain etc. |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | Carbon dioxide Supply System | [7 empty] | 1
3.01 | od250767/2022_2023 : Supply, Installation, Testing and commissioning of Fully Automatic Main CO2 supply system with manifold : Supply, Installation, testing and commissioning of Fully automatic gas control panel with flow capacity of 200LPM .Manifold capacity - 2 x 2 cylinder capacity (As per technicalspecification Standard: ISO 7396 / HTM 02-01)&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.02 | od250769/2022_2023 : Supply, Installation, Testing and commissioning of CO2 Manifold - 2 banks x 2 cylinders with with tail pipes, NRV, fixing chain etc.&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4 | Compressed Air Plant | [7 empty] | 1
4.01 | od250775/2022_2023 : Supply,Installation, testing and commissioning of Medical Air Plant consisting of 3 screw compressor compact super sound absorbing tower design and each compressors should have1000 LPM at 13 bar in free air delivery pattern.Twin vertical air receiver tank Capacity 1500 liters each, 2 Dryer and double filtration unit - 5-stage conditioning systems with filters and adsorption dryer and a pressure reducer station, electrical control panel. (Two set of medical air purification system as per the technical specification and air quality according to european pharmacopea.)Each compressor should have minimum FAD of 1000LPM (35CFM). Third party certification to be produced for medical grade air quality and compressor FAD capacity verification. |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5 | Vacuum Plant | [7 empty] | 1
5.01 | od250780/2022_2023 : &quot;&lt;br&gt;Supply, fixing, testing and commissioning of Medical grade Central Vacuum System Complete with Three rotary vane type Vacuum Pumps each having 2200 LPM at a pressure of 450mmHg. with motor , Filter, interconnecting pipes, NRV, auto switch gear assy,and common receiver 2 x 2000 liters (water capacity fabricated conforming to IS 2825 and material of construction should be IS 2062 plate).each vacuum pump should have FAA 2200 LPM at 450mmHg, &lt;br&gt;Dual Bacteria Filters shall have an efficiency at least 99.9999% in accordance withHTM 02-01 /ISO 7396. The system should supply with the electrical panel&quot;&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.02 | od250782/2022_2023 : Supply installation testing and commissioning of Electrical Control Panel for Air Compressor &amp; Vacuum Pump complete with plant Room wiring&lt;br&gt; |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6 | WAGD SYSTEM | [7 empty] | 1
6.01 | od250784/2022_2023 : Supply, Installation, Testing and commissioning of WAGD SYSTEM (meeting ISO 7396-2/HTM02-01)&lt;br&gt;Terminal Units |  | 9 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.02 | od250785/2022_2023 : Supply installation testing and commissioning of AGSS Hose Asembly, as per technical specification . |  | 30 | RM |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7 | Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) | [7 empty] | 1
7.01 | od250786/2022_2023 : Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) &lt;br&gt;1 Gases (O2) and 1 Vac (DN 20) with NIST Connection |  | 3 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.02 | od250797/2022_2023 : Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) &lt;br&gt;2 Gases (O2, Air) and 1 Vac (DN 20) with NIST Connection |  | 12 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.03 | od250799/2022_2023 : Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) &lt;br&gt;3 Gases (O2, Air4,N2O) and 1 Vac (DN 20) with NIST Connection |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.04 | od250800/2022_2023 : Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) &lt;br&gt;4 Gases (O2, Air4,Air 7, N2O) and 1 Vac (DN 20) with NIST Connection |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.05 | od250803/2022_2023 : Supply, installation, testing and commissioning of Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) &lt;br&gt;5 Gases (O2, Air4, Air 7,N2O, CO2) and 1 Vac with NIST Connection |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8 | Isolation valves | [7 empty] | 1
8.01 | od250805/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported &lt;br&gt;DN 15 - 15x1&lt;br&gt; |  | 36 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.02 | od250806/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported&lt;br&gt;DN 20 - 22x1 |  | 110 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.03 | od250807/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported &lt;br&gt;DN 25 - 28x1,5 |  | 44 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.04 | od250808/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported &lt;br&gt;DN 32 - 35x1,5 |  | 11 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.05 | od250810/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported &lt;br&gt;DN 42 - 54x1,5 |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8.06 | od250812/2022_2023 : Supply, installation, testing and commissioning of Ball valve with male screw threads and flat tightened solder unions, front ends with slots to incorporate o-ring, oil-free and degreased, for medical gases and vacuum, handle with safety device securing handle in operating position, marked acc. DIN EN 19. Please check technical specifications for complete details. - Imported &lt;br&gt;DN 80 - 76x1,5 |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9 | " Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings " | [7 empty] | 1
9.01 | od250813/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Oxygen (O2) |  | 250 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.02 | od250814/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Nitrous Oxide (N2O) |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.03 | od250816/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Medical Air 400 |  | 100 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.04 | od250817/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Surgical Air 700 |  | 25 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.05 | od250818/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Vacuum (Vac) |  | 250 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.06 | od250821/2022_2023 : Gas Outlet Points/ Terminal Unit (BS standard) : Supply,Installation, testing and commissioning of Gas outlet points for following Medical Gas as per specified in Tender schematic drawings &lt;br&gt;Carbon Dioxide (CO2) as per DIN standard |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10 | Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard. | [7 empty] | 1
10.01 | od250828/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;O2 |  | 220 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.02 | od251090/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;O2( Matching probe / adaptor shall be provided at one end suitable for Oxygen Gas Outlets and other end for ventillator) |  | 30 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.03 | od252001/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;Vacuum |  | 250 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.04 | od252085/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;MA4 |  | 100 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.05 | od252094/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;N2O |  | 9 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.06 | od252095/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;SA7 |  | 25 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.07 | od252096/2022_2023 : Supply, installation of Matching Probe/adopter with one end suitable for Hose &amp; other end suitable for terminal units which complies and fully meets with the latest standard.&lt;br&gt;Co2 |  | 8 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11 | Bed head panels | [7 empty] | 1
11.01 | od250838/2022_2023 : Supply, installation, testing and commissioning of Horizontal Bed Head Panels of 3 feet long with provision for 3 nos electrical (power &amp; data) &amp; min 3 nos Gas outlets - as per technical specification for Post operative beds |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.02 | od250841/2022_2023 : Supply, installation, testing and commissioning of Horizontal Bed Head Panels of 4 feet long with provision for 3 nos electrical (power &amp; data) &amp; min 5 nos Gas outlets - as per technical specification for ICU beds |  | 30 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.03 | od250849/2022_2023 : Supply, installation, testing and commissioning of Continous Bed head panel with provision for fixing Medical gas outlets, power sockets, nurse cal points etc. as per the design requirement. |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12 | Medical Equipments | [7 empty] | 1
12.01 | od250850/2022_2023 : Supply, installation, testing and commissioning of Oxygen Flow meter with humidifier bottle 0-15 litres.. Matching probe / adaptor shall be provided at one end suitable for Oxygen Gas Outlets and other end for flow meter. |  | 250 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.02 | od250851/2022_2023 : Suply installation testing and commissiong of Ward Vacuum Unit which consists of the following :- 1no. Suction Regulator and 1no. 1000ml polysulphone collection jar. Suction Regulator : Suction regulator should be supplied with a safety jar, including and antibacterial filter and an anti overflow safety device. Should have wide membrane continuous suction controller. It Should have vacuum levels : 0-1000mbar/hPa. Should have vacuum gauge fitted with a protective bumper device. Should have on/off knob allowing for the quick restoration of a readjusted vacuum level with one end suitable for vacuum gas outlets and other end for Vacuum Hose. |  | 250 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.03 | od250904/2022_2023 : Supply installation, testing and commissioning of Theatre Suction Unit.It must consists of the following :- 1no. Suction Regulator and 2nos. 2000ml polysulphone collection jar and both to be mounted on a trolley. Suction Regulator : Suction regulator should be supplied with a safety jar, including and antibacterial filter and an anti overflow safety device. Should have wide membrane continuous suction controller. It Should have vacuum levels : 0-1000mbar/hPa. Should have vacuum gauge fitted with a protective bumper device. Should have on/off knob allowing for the quick restoration of a readjusted vacuum level. Theatre Suction Unit with 3200 ml jars as per specifications. Matching probe / adaptor shall be provided at one end suitable for Vacuum Gas outlets and other end for Vacuum Hose including trolley.&lt;br&gt; |  | 10 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.04 | od250949/2022_2023 : Supply installation testing and commissioning of Medical gas hose assemblies shall comply with BS EN 739. Hoses shall be color coded throughout their length as specification: High pressure Hose antistatic duly colour coded for Oxygen , Nitrous Oxide, Medical Air and Vacuum as per technical specification .Certificate of Origin must be given. |  | 250 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13 | Master plant alarm - Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) | [7 empty] | 1
13.01 | od250914/2022_2023 : Supply, installation, testing and commissioning of Master plant alarm&lt;br&gt;Master plant alarm - Integrated area alarm with Valve Box (Including valves) and gauge (should comply EN ISO 7396 and BMS compatiblity) |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13.02 | od124159/2024_2025 : Supply, Installation, Testing and Commissioning of Surgeon&apos;s Pendant - 1750mm Double Arm along with high pressure flexible hoses and necessary NIST adapters. (Provision for 10 electrical + 4 data + 3 Shelf + Provision for Gas outlets with terminal units) |  | 4 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13.03 | od124160/2024_2025 : Supply, Installation, Testing and Commissioning of Anaesthesia Pendant - 1000mm Single Arm along with high pressure flexible hoses and necessary NIST adapters. (Provision for 10 electrical + 4 data + 1 Shelf + 1 IV pole + Provision for Gas outlets with terminal units) |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14 | Copper Piping As per EN13348 standards. | [7 empty] | 1
14.01 | od250925/2022_2023 : &quot;Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;12mm OD x 1mm thick copper pipe |  | 700 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.02 | od250929/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;15mm OD x 1mm thick copper pipe |  | 1800 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.03 | od250931/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;22mm OD x 0.9mm thick copper pipe |  | 980 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.04 | od250934/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;28mm OD x 0.9mm thick copper pipe &lt;br&gt; |  | 396 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.05 | od250935/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;35mm OD x 1.2mm thick copper pipe |  | 250 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.06 | od250936/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;42mm OD x 1.2mm thick copper pipe |  | 150 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.07 | od250937/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;54mm OD x 1.2mm thick copper pipe |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
14.08 | od250938/2022_2023 : Supply,Installation testing and commissiong of Medical Grade LLOYD certified Copper Pipes : Copper pipes manufactured from phosphorous de-oxidised non-arsenical copper to BS EN 1412:1996 grade and having mechanical properties in accordance with BS EN 13348:2008 in either R250 (half hard) or R290 (hard). Degreasing of pipe shall be such that there is less than 20mg/m2 (0.002mg/cm2) of hydrocarbons on the degreased surface when tested by the method specified BS EN 13348:2008&lt;br&gt;76mm OD x 1.5mm thick copper pipe |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information