## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: WAPCOS Limited
Work Name : District TB Center, Idukki- Civil Works
Contract No: WAP/INFRA/KERALA/2024/IKKI/476
Bidder Name :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Civil works | BI01010001010000000000000515BI0100001111 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | 2.8.1 : Earth work in excavation by mechanical means (Hydraulic excavator) /manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift up to 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m.All kinds of soil |  | 743.785 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 2.6.1 : Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead up to 50 m and lift up to 1.5 m, disposed earth to be levelled and neatly dressed.All kinds of soil |  | 1329.49 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | 2.25 : Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m.Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m. |  | 249.628 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.04 | 2.34.1 : Supplying chemical emulsion in sealed containers including delivery as specified.Chlorpyriphos / Lindane emulsifiable concentrate of 20% |  | 185.742 | Litre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.05 | 2.35.3.1 : Diluting and injecting chemical emulsion for POST -CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion):Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1:2 (1 cement : 2 coarse sand) to match the existing floor:With Chlorpyriphos/Lindane E.C. 20% with 1% concentration |  | 309.579 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.06 | 4.1.8 : Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level:1:4:8 (1 cement : 4 coarse sand : 8 graded stone aggregate 40 nominal size) |  | 102.713 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | 4.11 : Providing and laying damp-proof course 50 mm thick with cement concrete 1:2:4(1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). |  | 40.361 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.08 | od5081/2023_2024 : Providing &amp; applying a coat of residual petroleum bitumen of grade of VG-10&lt;br&gt;of approved quality using 1.7kg per square metre on damp proof course after&lt;br&gt;cleaning the surface with brushes and finally with apiece of cloth lightly&lt;br&gt;soaked in kerosene oil. |  | 40.361 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.09 | 5.9.1 : Centering and shuttering including strutting, etc. and removal of form for:Foundations, footings, bases of columns, etc for mass concrete |  | 377.687 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.1 | 5.9.2 : Centering and shuttering including strutting, etc. and removal of form for:Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. |  | 287.22 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | 5.9.3 : Centering and shuttering including strutting, etc. and removal of form for:Suspended floors, roofs, landings, balconies and access platform |  | 773.853 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | 5.9.5 : Centering and shuttering including strutting, etc. and removal of form for:Lintels, beams, plinth beams, girders bressumers and cantilevers |  | 1720.635 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | 5.9.6 : Centering and shuttering including strutting, etc. and removal of form for:Columns, Pillars, Piers, Abutments, Posts and Struts |  | 711.472 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | 5.9.7 : Centering and shuttering including strutting, etc. and removal of form for:Stairs, (excluding landings ) except spiral - staircases) |  | 46.44 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | 5.9.16.1 : Centering and shuttering including strutting, etc. and removal of form for:Edges of slabs and breaks in floors and wallsUnder 20 cm wide |  | 255.6 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | 5.9.19 : Centering and shuttering including strutting, etc. and removal of form for:Weather shade, Chajjas, corbels etc., including edges |  | 89.828 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | od97573/2023_2024 : Providing and fixing S.S fan clamp of 10mm dia in RCC slabs , beams including cost and conveyance of all materials,labour charges etc complete as directed by the Engineer - in - Charge at all levels |  | 35 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | 5.22.6 : Steel reinforcement for R.C.C work including straightening, cutting, bending, placing in position and binding all complete upto plinth levelThermo - Mechanically Treated bars of grade Fe-500D or more |  | 67820 | kilogram |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | 5.33.1 : Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer - in-charge. Note:- Cement content considered in this item is @ 330 kg/ cum. Excess or less cement used as per design mix is payable or recoverable separately.All work upto plinth level |  | 244.398 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | 5.33.2 : Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer - in-charge. Note:- Cement content considered in this item is @ 330 kg/ cum. Excess or less cement used as per design mix is payable or recoverable separately.All work above plinth level upto floor V level |  | 346.367 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | od259703/2023_2024 : Providing and laying in position machine batched and machine mixed design mix&lt;br&gt;M-30 grade cement concrete for reinforced cement concrete work, using cement&lt;br&gt;content as per approved design mix, including pumping of concrete to site of laying&lt;br&gt;but excluding the cost of centering, shuttering, finishing and reinforcement,&lt;br&gt;including admixtures in recommended proportions as per IS: 9103 to accelerate,&lt;br&gt;retard setting of concrete, improve workability without impairing strength and&lt;br&gt;durability as per direction of Engineer-in-charge.&lt;br&gt;All works above plinth level upto floor V level |  | 10.133 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | od259704/2023_2024 : Providing and laying in position machine batched and machine mixed design mix&lt;br&gt;M-30 grade cement concrete for reinforced cement concrete work, using cement&lt;br&gt;content as per approved design mix, including pumping of concrete to site of laying&lt;br&gt;but excluding the cost of centering, shuttering, finishing and reinforcement,&lt;br&gt;including admixtures in recommended proportions as per IS: 9103 to accelerate,&lt;br&gt;retard setting of concrete, improve workability without impairing strength and&lt;br&gt;durability as per direction of Engineer-in-charge.&lt;br&gt;All works upto plinth level |  | 29.857 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | 50.6.1.1 : Solid block masonry using pre cast solid blocks ( factory made) of size 40x20x20cm or nearest available size confirming to IS 2185 part 1 of 1979 for foundation and plinth with thickness 20 cm and above in: CM 1:6 ( 1 cement : 6 coarse sand) etc complete |  | 4.06 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | 50.6.1.2 : Solid block masonry using pre cast solid blocks (Factory made) of size 40x20x20cm or nearest available size confirming to IS 2185 part I of 1979 for super structure up to floor two level thickness 20cm and above in: CM 1:6 ( 1 cement: 6 coarse sand) etc complete. |  | 248.076 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | 6.13.1 : Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:3 (1 cement : 3 coarse sand) |  | 60.618 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | 6.15 : Extra for providing and placing in position 2 Nos 6 mm dia M.S bars at every third course of half brick masonry. |  | 60.618 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | 10.25.2 : Item Shifted to head 14 as item 14.74Steel work welded in built up sections/framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required.In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works |  | 610.4 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | 13.1.1 : 12 mm cement plaster of mix:1:4 ( 1 cement : 4 fine sand) |  | 2524.689 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | 13.2.1 : 15 mm cement plaster on the rough side of single or half brick wall of mix:1:4 (1 cement :4 fine sand) |  | 966.18 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | 13.8.2 : 15 mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix:1: 4 ( 1 cement : 4 fine sand) |  | 97.5 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | 13.16.1 : 6 mm cement plaster of mix:1:3 ( 1 cement : 3 fine sand) |  | 896.773 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | 22.5 : Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours. b) Second layer of slurry of cement @ 0.242 kg /sqm mixed with water proofing cement compound @ 0.126 kg/ sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours. The rate includes preparation of surface, treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry. |  | 29.805 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | od291085/2023_2024 : Brick jelly Concrete in Cement Mortar 1:3:6 using 40 mm broken bricks in sunken areas including cost,conveyance,labour charges etc. ... complete as per the direction from Engineer in Charge |  | 4.473 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | 22.6 : Providing and laying water proofing treatment on roofs of slabs by applying cement slurry mixed with water proofing cement compound consisting of applying : a) after surface preparation, first layer of slurry of cement @ 0.488 kg/ sqm mixed with water proofing cement compound @ 0.253 kg/ sqm. laying second layer of fibre glass cloth when the first layer is still green. Overlaps of joints of fibre cloth should not be less than 10 cm. c) third layer of 1.5 mm thickness consisting of slurry of cement @ 1.289 kg/ sqm mixed with water proofing cement compound @ 0.670 kg/sqm and coarse sand @ 1.289 kg/sqm. This will be allowed to air cure for 4 hours followed by water curing for 48 hours. The entire treatment will be taken upto 30 cm on parapet wall and tucked into groove in parapet all around. d) fourth and final layer of brick tilling with cement mortar (which will be paid for separately. For the purpose of measurement the entire treated surface will be measured) |  | 650 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | 11.41.2 : Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20 mm thick cement mortar 1:4(1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600 x 600 mm. |  | 719.605 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.36 | 11.46.2 : Providing and laying Vitrified tiles indifferent sizes (thickness to be specified by manufacturer), with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make, in all colours & shade, in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm |  | 47.934 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.37 | 11.19.4 : Chequered terrazo tiles 22 mm thick with graded marble chips of size up to 6 mm in floors, jointed with neat cement slurry mixed with pigment to match the shade of the tiles, including rubbing and polishing complete, on 20 mm thick bed of cement mortar 1:4 ( 1 cement : 4 coarse sand):Ordinary cement without any pigment |  | 13.8 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.38 | 11.39 : Providing and laying rectified Glazed Ceramic floor tiles of size 300x300 mm or more (thickness to be specified by the manufacturer), of 1st quality conforming to IS: 15622, of approved make in colours White, Ivory, Grey, fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 cement : 4 Coarse sand), including grouting the joints with white cement and matching pigments etc., complete. |  | 25.164 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.39 | 8.31 : Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineerin-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 106.266 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.4 | 11.56.1 : Providing and laying Polished Granite stone flooring in required design and patterns, in linear as well as curvilinear portions of the building all complete as per the architectural drawings with 18 mm thick stone slab over 20 mm (average) thick base of cement mortar 1:4 (1 cement : 4 coarse sand) laid and jointed with cement slurry and pointing with white cement slurry admixed with pigment of matching shade including rubbing , curing and polishing etc. all complete as specified and as directed by the Engineer-in-Charge.Polished Granite stone slab jet Black, Cherry Red, Elite Brown, Cat Eye or equivalent. |  | 37.262 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.41 | 9.1.1 : Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately).Second class teak wood |  | 0.086 | cum |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.42 | 9.5.1.2 : Providing and fixing panelled or panelled and glazed shutters for shutters for doors, windows and clerestory windows, including ISI marked M.S. pressed butt hinges bright finished of required size with necessery screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer - in-charge.Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note:- Butt hinges and necessary screws shall be paid separately) Second class teak wood 30 mm thick shutters |  | 9.24 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.43 | 21.1.1.2 : Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS : 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminnium snap beading for glazing /paneling, C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge.(Glazing, paneling and dash fasteners to be paid for separately):For fixed portionPowder coated aluminium (minimum thickness of powder coating 50 micron) |  | 467.901 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.44 | 21.1.2.2 : For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber/ neoprene gasket required (Fittings shall be paid for separately)Powder coated aluminium (minimum thickness of powder coating 50 micron) |  | 611.1 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.45 | 21.2.2 : Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS : 12823 Grade I Type II, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of Engineer - in- Charge.Pre- laminated particle board with decorative lamination on both sides |  | 18.151 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.46 | 21.3.1 : Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of Engineer - in -Charge. ( Cost of aluminium snap beading shall be paid in basic item):With float glass panes of 4.0 mm thickness |  | 403.68 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.47 | 9.95.3 : Providing and fixing ISI marked aluminium butt hinges anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc. complete:100x75x4 mm |  | 124 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.48 | 9.97.3 : Providing and fixing aluminium tower bolts, ISI marked, anodised(anodic coating not less than grade AC 10 as per : 1868), transparent or dyed to required colour or shade, with necessary screws complete:200x10 mm |  | 33 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.49 | 9.100.1 : Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete:125 mm |  | 41 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.5 | 9.101.1 : Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete.Single rubber stopper |  | 38 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.51 | 9.102 : Providing and fixing aluminium casement stays, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. |  | 87 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.52 | 9.103 : Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS: 1868) aluminium lever handles of approved quality with necessary screws etc . complete. |  | 12 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.53 | 9.117.1 : Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1 mm), with wall thickness 2.0mm (±0.2 mm), corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joints mitred and plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 x 19 mm and 1 mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer's specification and direction of Engineer-in-chargeExtruded section profile size 48x40 mm |  | 61.2 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.54 | 9.120.1 : Providing and fixing factory made panel PVC door shutter consisting of frame made out of M.S. tubes of 19 gauge thickness and sized of 19 mm x 19 mm for styles and 15x15 mm for top & bottom rails. M.S. frame shall have a coat of steel primers of approved make and manufacture. M.S. frame covered with 5 mm thick heat moulded PVC 'C' channel of size 30 mm thickness, 70 mm width out of whicj 50 mm shall be flat and 20 mm shall be tapered in 45 degree angle on both side forming styles and 5mm thick, 95 mm wide PVC sheet out of which75 mm shall be tapered in 45 degree on th inner side to form top and bottom rail and 115 mm wide PVC sheet out of which 75 mm shall be flat and 20 mm shall be tapered on both sides to form lock rail. Top, bottom and lock rails shall be provided both side of the panel. 10 mm (5 mmx2) thick, 20 mm wide cross PVC sheet be provided as gap insert for top rail & bottom rail. paneling of 5 mm thick both side PVC sheet to be fitted in the M.S. frame welded /sealed to the styles & rails with 7 mm (5 mm + 2 mm ) thick x 15 mm wide PVC sheet beading on inner side, and joined together with solvent cement adhesive. An additional 5 mm thick PVC strip of 20 mm width is to be stuck on the interior side of the 'C' Channel using PVC solvent adhesive etc. complete as per direction of Engineer -in-charge, manufacture's specification & drawing.30 mm thick plain PVC door shutters |  | 22.68 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.55 | 13.43.1 : Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface:Water thinnable cement primer |  | 3307.071 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.56 | 13.47.1 : Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade:New work (Two or more coats applied @ 1.43 ltr/ 10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) |  | 1053.9 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.57 | 13.60.1 : Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade:Two or more coats on new work |  | 3307.071 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.58 | 13.114 : Melamine polishing on wood work (one or more coat). |  | 82.959 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.59 | 10.28 : Providing and fixing stainless steel (Grade 304) railing made of Hollow tubes, channels, plates etc., including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete, i/c fixing the railing with necessary accessories & stainless steel dash fasteners, stainless steel bolts etc., of required size on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge, (for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.) |  | 163.711 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | Plumbing works | BI01010001010000000000000515BI0100001112 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.01 | 17.2.1 : Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required:W.C. pan with ISI marked white solid plastic seat and lid |  | 11 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.02 | 18.21.1.1 : Providing and fixing uplasticised PVC connection pipe with brass unions:30 cm length15 mm nominal bore |  | 26 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.03 | 50.17.1.5 : Supplying and fixing CP Health Faucet superior quality ( Jagur or equvalent make ) including cost of materials and labour charges etc complete as per the direction of site Engineer-in-charge. |  | 11 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | 17.7.4 : Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require:White Vitreous China Flat back wash basin size 550x400mm with single 15 mm C.P.brass pillar taps |  | 12 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.05 | 17.10.2.1 : Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink as per IS 13983 with C.I. brackets and stainless steel plug 40 mm, including painting of fittings and brackets, cutting and making good the walls wherever required:Kitchen sink without drain board610x510 mm bowl depth 200 mm |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.06 | 17.73.2 : Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88 mm, weighting not less than 190 gms |  | 11 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.07 | 18.8.2 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes& fittings, with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc.20 mm nominal outer dia pipes |  | 31 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.08 | 18.8.3 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes& fittings, with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc.25 mm nominal outer dia pipes |  | 17 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.09 | 18.8.4 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes& fittings, with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc.32 mm nominal outer dia pipes |  | 19 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.1 | 18.7.3 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall25 mm nominal outer dia pipes |  | 7 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.11 | 18.7.4 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall32 mm nominal outer dia pipes |  | 57 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.12 | 18.7.5 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall40 mm nominal outer dia pipes |  | 5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.13 | 18.7.6 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer -in-Charge. Internal work - Exposed on wall50 mm nominal outer dia pipes |  | 66 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.14 | 18.9.6 : Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer- in-Charge. External work50 mm nominal outer dia pipes |  | 11 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.15 | 50.18.7.4.2 : Providing and fixing PVC, pipes fittings including fixing the pipe with clamps at 1.00 m spacing. this includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 32 mm dia 6 Kgf/cm2 - internal work- Exposed on wall |  | 8.5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.16 | 50.18.7.5.2 : Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 40 mm dia 6Kgf/cm2 - Internal work - Exposed on wall |  | 2.5 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.17 | 50.18.8.6.2 : Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Concealed work, including cutting chases and making good the wall etc. 50 mm pipe 6 kgf/cm2 |  | 41 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.18 | 50.18.7.6.2 : Providing and fixing PVC pipes, fittings including fixing the pipe with clamps at 1.00 m spacing . This includes jointing of pipes & fittings with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 50 mm dia 6 Kgf/cm2 - Internal work- Exposed on wall |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.19 | 50.18.9.17.2 : Providing and fixing PVC pipes including fixing the pipe with clamps/clips at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 63 mm dia 4 Kgf/cm2- External work - exposed on wall |  | 44 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.2 | 50.18.9.18.1 : Providing and fixing PVC pipes including fixing the pipe with clamps/clips at 1.00 m spacing. This included jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 75 mm dia 6Kgf/cm2 - External work- Exposed on wall |  | 75 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.21 | 50.18.9.19.1 : Providing and fixing PVC pipes including fixing the pipe with clamps/ clips/ at 1.00 m spacing . This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 110 mm dia 6 Kgf/cm2 - External work- Exposed on wall |  | 66 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.22 | 50.18.9.8.1 : Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. 75 mm dia 6 Kgf/ cm2 |  | 28 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.23 | 50.18.9.9.1 : Providing and fixing PVC pipes includings jointing of pipes with one step PVC solvent cement, trenching, refilling & testing of Joints complete as per direction of engineer in charge.110 mm dia 6Kgf/cm2 |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.24 | 50.18.9.19.2 : Providing and fixing PVC pipes including fixing the pipe with clamps/clips at 1.00 m spacing. This includes jointing of pipes with one step PVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge 110 m dia 4 Kgf/cm2 - External work - Exposed on wall |  | 80 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.25 | 18.17.1A : Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :20 mm nominal bore |  | 1 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.26 | 18.17.1 : Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :25 mm nominal bore |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.27 | 18.17.2 : Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :32 mm nominal bore |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.28 | 18.17.3 : Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :40 mm nominal bore |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.29 | 18.17.4 : Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :50 mm nominal bore |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.3 | 18.51.1 : Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore |  | 11 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.31 | 18.52.1 : Providing and fixing C.P brass stop cock ( concealed) of standard design and of approved make conforming to IS: 893115 mm nominal bore |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.32 | 18.53.1 : Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS: 893115 mm nominal bore |  | 37 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.33 | od17419/2023_2024 : Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand) with R.C.C. top with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size,) inside plastering 12 mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) finished with a floating coat of neat cement complete as per standard design:Inside size 60x60 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weigh of cover 23 kg and weight of frame 15 kg):With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.34 | 19.7.1.1 : Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand) with R.C.C. top with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size,) inside plastering 12 mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) finished with a floating coat of neat cement complete as per standard design:Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weigh of cover 23 kg and weight of frame 15 kg):With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.35 | od17418/2023_2024 : Extra for depth for manholes Size 60x60 cm: With common burnt clay F.P.S. ( non modular ) bricks of class designation 7.5 |  | 0.6 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.36 | 19.8.1.1 : Extra for depth for manholesSize 90x80 cmWith common burnt clay F.P.S. ( non modular ) bricks of class designation 7.5 |  | 1 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.37 | 19.4.1.1 : Providing and fixing square-mouth S.W. gully trap class SP -1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design:100x100 mm size P typeWith common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 6 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.38 | 19.32.1 : Making soak pit 2.5 m diameter 3.0 metre deep with 45 x 45 cm dry brick honey comb shaft with bricks and S.W. drain pipe 100 mm diameter, 1.8 m long complete as per standard design.With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.39 | od17416/2023_2024 : Providing and fixing PVC moulded fittings /accessories for Rigid PVC pipes, including jointing with PVC solvent cement -Multi-Inlet Floor traps |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.4 | 50.18.9.10.1 : Providing and fixing PVC pipes includings jointing of pipes with one step pvc solvent cement, trenching , refilling & testing of joints complete as per direction of Engineer in Charge. 150 mm dia 6 Kgf/cm2 |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.41 | 19.18.2 : Supplying and fixing C.I with out frame for manholes:500 mm diameter C.I. (medium duty) the weight of the cover to be not less than 58 kg |  | 9 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.42 | od17421/2023_2024 : Supply, Installation, Testing and Commissioning of open well submersible type water transfer pump of capacity 120LPM at required head (I duty + 1 standby) for pumping domestic water from UGT to OHT with CI body, Bronze Impeller and IE3 efficiency class motor including control panels, valves, level switches, power and control cables, stator switch etc. complete for fixed installation.&lt;br&gt;Open well submersible pumps 120LPM@ 40m head (I duty + 1 standby) |  | 1 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | MV CABLE SUPPLY | BI01010001010000000000000515BI0100001113 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.01 | od15934/2023_2024 : Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date. &lt;br&gt;2cx2.5sq.mm Cu Control Cable (2XFY)&lt;br&gt; |  | 55 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.02 | od15935/2023_2024 : Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, unarmoured copper conductor power cable &lt;br&gt;1cx16sq.mm Cu Cable (2XFY)&lt;br&gt; |  | 88 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.03 | 90.12.1.35 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.04 | 90.12.1.41 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 15 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.05 | 90.12.1.42 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 16 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.06 | 90.12.1.40 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 90 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.07 | 90.12.6.39 : Supply & laying of one No. PVC insulated and PVC sheathed armoured aluminium power cable of 1.1 KV grade of the following sizes in the existing masonry open duct as required. |  | 30 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.08 | 90.12.1.38 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 100 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.09 | 90.12.1.1 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 31 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.1 | 90.12.1.32 : Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil). |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4 | MV CABLE LAYING | BI01010001010000000000000515BI0100001114 | [6 empty] | 1
4.01 | 7.5.3 : Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.Above 95 sq. mm and upto 185 sq. mm |  | 33 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.02 | 7.7.1 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.Upto 35 sq. mm (clamped with 1mm thick saddle) |  | 94 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.03 | 7.7.4 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) |  | 10 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.04 | 7.8.1 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.Upto 35 sq. mm (clamped with 1mm thick saddle) |  | 448 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.05 | 7.8.2 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) |  | 33 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.06 | 7.8.3 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) |  | 22 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.07 | 7.8.4 : Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) |  | 28 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.08 | 7.10 : Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. |  | 5 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
4.09 | 7.1.1 : Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.Upto 35 sq. mm |  | 300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5 | MV CABLE END TERMINATION | BI01010001010000000000000515BI0100001115 | [6 empty] | 1
5.01 | 9.1.34 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 25 sq. mm (28mm) |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.02 | 9.1.32 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 10 sq. mm (25mm) |  | 8 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.03 | od15937/2023_2024 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;4 X 6 sq. mm (25mm)&lt;br&gt; |  | 19 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.04 | od15938/2023_2024 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;4 X 4 sq. mm (19mm)&lt;br&gt; |  | 10 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.05 | od15940/2023_2024 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;2 X 4 sq. mm (19mm)&lt;br&gt; |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.06 | od15941/2023_2024 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;2cx2.5sq.mm Cu Control Cable (19mm) - with copper lugs&lt;br&gt; |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.07 | od15942/2023_2024 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.&lt;br&gt;1c X 16sq.mm Cu Cable (22mm) - with copper lugs&lt;br&gt; |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.08 | 9.1.31 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 400 sq. mm (82mm) |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.09 | 9.1.33 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.4 X 16 sq. mm (28mm) |  | 6 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.1 | 9.1.25 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2 X 120 sq. mm (45mm) |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
5.11 | 9.1.29 : Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.3 1/2X 240 sq. mm (62mm) |  | 2 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6 | LIGHT FIXTURES | BI01010001010000000000000515BI0100001116 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.01 | od15882/2023_2024 : Supply of surface mountable, LED Batten Luminaire with Minimum 1800 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 20W, Luminaire Housing shall be CRCA/aluminium with polycarbonate Diffuser with minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection integrated in driver, PF&ge;0.95,and total harmonic distortion THD&le;20%. BIS approved , including all accesories as required . (Approved Make - Philip BN100C LED20S-6500 PSU L120 GR S4 / Havells STOUT Plus 20W / Wipro LL24-251-XXX-57-XX / Equvalent model from approved makes list)&lt;br&gt; |  | 34 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6.02 | od15883/2023_2024 : Supply of recess mountable, low height, LED downlight fixture with Minimum 1500 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 15W, Luminaire Housing shall be aluminium die cast with polycarbonate Diffuser with minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection, PF&ge;0.95,and total harmonic distortion THD&le;10%. BIS approved , including all accesories as required . (Approved Make - Philips DN296B LED15S-6500 PSU WH / Havells Integra Next 15 W recessed / LD06-171-XXX-57-XX / Equvalent model from approved makes list)&lt;br&gt; |  | 24 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
6.03 | od15884/2023_2024 : Supply of recess mountable, low height, LED downlight fixture with Minimum 1200 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 12W, Luminaire Housing shall be aluminium die cast with polycarbonate Diffuser with minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection, PF&ge;0.95,and total harmonic distortion THD&le;10%. BIS approved , including all accesories as required . (Approved Make - Philips DN296B LED12S-6500 PSU WH / Havells Integra Next 12 W recessed / Wipro LD06-151-XXX-57-XX / Equvalent model from approved makes list)&lt;br&gt; |  | 15 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.04 | od15885/2023_2024 : VSupply of surface mountable, LED downlight fixture with Minimum 1500 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 15W, Luminaire Housing shall be with polycarbonate cover for mounting with Diffuser and minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection, PF&ge;0.95,and total harmonic distortion THD&le;10%. BIS approved , including all accesories as required . (Approved Make - Philips SM251C LED16S 6500 PSU / Havells Endura HE DL Surfaced 15 W / Wipro LD06-171XXX-57SMG1 / Equvalent model from approved makes list)&lt;br&gt; |  | 25 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.05 | od15886/2023_2024 : Supply of recess mountable, low height, LED 2x2 light fixture with Minimum 3600 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 36W, Luminaire Housing shall be CRCA with polycarbonate Diffuser with minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection, ripple content&lt;5%, PF&ge;0.95,and total harmonic distortion THD&le;10%. BIS approved , including all accesories as required . (Approved Make - Philips RC380B LED36S-6500 G6 L60W60 PSU OD / Havells Venus Neo 2x2 36 W / Wipro CRCO10R038HP57G1L5 / Equvalent model from approved makes list)&lt;br&gt; |  | 35 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.06 | od15887/2023_2024 : Supply of surface mountable, LED 2x2 light fixture with Minimum 3600 Lumens output with System efficacy =&gt; 100 Lumen/Watts. Total wattage of fixture to be limited to 36W, Luminaire shall be with polycarbonate / CRCA outer cover for surface mounting and polycarbonate Diffuser with minimum IP20 protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80 and CCT &gt;= 5700K. The luminaire must have minimum 2KV surge protection, ripple content&lt;5%, PF&ge;0.95,and total harmonic distortion THD&le;10%. BIS approved , including all accesories as required . (Approved Make - Philips RC380B LED36S-6500 G6 L60W60 PSU OD + Surface Kit / Havells PLUTO SURFACE 2x2 / Wipro CRCO10S038HP57GL1 / Equvalent model from approved makes list)&lt;br&gt; |  | 51 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.07 | od15890/2023_2024 : Supply of Led Bulk head surface mountable with System efficacy&gt; 90 Lumen/Watt and Housing Shall be made of strong body for outdoor application to avoid rusting and Polycarbonator diffuser to reduce glare with IP66 and IK09 Protection. The Luminaire should be having Minimum 50,000 Burning hours with CRI &ge;80, (CCT) &gt; 5700K. The luminaire should have minimum 2KV surge protection integrated in driver, PF&ge;0.95, Total harmonic distortion THD&le;10% including all accesories as required . (Approved Make - Wipro LW07-141-XXX-57-XX / Havells HEXA 10 W / Equvalent model from approved makes list)&lt;br&gt; |  | 20 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
6.08 | od17429/2023_2024 : Supply, fixing, testing and commissioning of 6 M octagonal poles of approved Make having top dia 70 mm, bottom dia 130 mm, Sheet thickness 3 mm, pitch circle dia (PCD) of 200 mm, Base plate dimentions 200mm length x 200mm bredth x 12mm thickness, EN8 grade Foundation bolts of size 4 x 20 mm dia, having bolt length of 600 mm. The Octagonal Poles shall be designed to withstand the maximum wind speed as per IS 875. The pole shaft shall have octagonal cross section and shall be continuously tapered with single longitudinal welding. There shall not be any circumferential welding. The octagonal Poles shall have door of approximate 500 mm length at the elevation of 500 mm from the Base plate. The door shall be vandal resistance and shall be weather proof to ensure safety of inside connections. The door shall be flush with the exterior surface and shall have suitable locking arrangement. There shall also be suitable arrangement for the purpose of earthing. Material Octagonal Poles HT Steel Conforming to grade S355JO.Base Plate Fe 410 conforming to IS 226 / IS 2062Foundation Bolts EN.8 grade (Make - Bajaj, Lighting Technologies, GE or equivalent). The poles shall be hot dip galvanised as per IS 2629 / IS 2633 / IS 4759 standards with average coating thickness of 85 micron. The galvanizing shall be done in single dipping. The pole shall include one arm for fixing including supply of minimum 4500 lumen output LED Street light with &gt;=100Lumen/Watt efficacy minimum, CRI &gt;70 , CCT&gt;5700 K , pf&gt;0.95. The luminaire must have a IP66 protection and IK07 protection minimum, and minimum 2 kV internal surge protection. BIS certified including all accesories required for complete installation (Make Philips BRP056 LED47 CW SLF PSU S1 / Wipro LR06-611-XXX-57-XX / Havells ENDURA OMNI PLUS 45W / Equvalent model from approved makes list)&lt;br&gt; |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7 | FAN IXTURES | BI01010001010000000000000515BI0100001117 | [6 empty] | 1
7.01 | od15891/2023_2024 : Supply of 5 star rated , BEE certified 26W, ceiling fan with BLDC motor,remote control for operation, with super enamelled copper wire winding, 230 V, single phase 50 HZ remote control operated fan with 1200mm sweep and 3 blades including all accessories as required with remote and standard length downrod all accesories required for complete installation (Havells Efficienca Neo or equivalent)&lt;br&gt; |  | 35 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.02 | od15892/2023_2024 : Supply, installation, testing and commisiong of 450mm sweep wall fan on surface including mouting and providing all accessories required for complete installation, testing, commisioning etc as required complete (Havells Airboll Hi-Speed or equivalent)&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.03 | od15893/2023_2024 : Supply of heavy duty exhaust fan of 450mm sweep in the existing opening, including making good the damage, connection, testing, commissioning etc. as required, including all accessories as rquired for complete installation incluidng shutter etc complete as required.(havells, TurboForce SP or equivalent)&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
7.04 | 1.44 : Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. |  | 35 | no |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
8 | 20kVA UPS | BI01010001010000000000000515BI0100001118 | [6 empty] | 1
8.01 | od15894/2023_2024 : 20 kVA UPS &lt;br&gt;&quot;Supply installation, testing and commissioning of following three phase to three phase 20kVA UPS indoor (IP20) in stand alone configuration,true online double conversion DSP based UPS system in stand alone configuration with inbuilt parallel kit capable of connecting UPS in parallel mode when required without additional cost, with 15 min backup battery ( battery of reputed make) with, input pf&gt;.99, less input current consumption, with necessary battery circuit breaker., with input 415V, 50Hz three phase, output 240V, IGBT rectifier and IGBT inverter. It shall be 100% generator compatabile with efficiency &gt; 94% and output power factor &gt; 0.9 and including all accessories etc as required. THe UPS system shall be with automatic&lt;br&gt;&amp; manual maintenance bypass switch facility.UPS shall have seperate battery bank, and batteries shall be connected in single string.The system shall comply to IEC /EN 62040-1 and relevant IS standard.The acoustic noise of the system should be less than 58dB.The system shall comply to IEC /EN 62040-1, EN/IEC 62040-2, EN/IEC 62040-3 and relevant IS standard. &lt;br&gt;&quot;&lt;br&gt;20kVA UPS - 1No Battery circuit Breaker-1No Battery - Required nos. of SMF for providing 15 Minutes Back UP and Battery Accessories like battery rack, interconnecting cables etc.&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9 | INTERNAL WIRING | BI01010001010000000000000515BI0100001119 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.01 | 1.10.3 : Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.Group C |  | 132 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.02 | 1.55.3 : Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point ( without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed PVC conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required.Group C |  | 70 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.03 | 1.11 : Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. |  | 4 | point |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.04 | od15673/2023_2024 : Wiring for Staircase Light Point (UPS POWERED)&lt;br&gt;Wiring for stair case light points with 2.5 sq.mm FRLS PVC insulated copper conductor single core cable in and including surface / recessed medium class PVC conduit and all acessories required for complete installation etc , with 1 way modular switch, modular plate, suitable GI box medium class PVC conduit and all acessories required etc and earthing the point with 2.5 sq.mm FRLS PVC insulated copper conductor single core cable etc as required and instructed by engineer in charge/consultant. (*Note - Staircase light point shall be controlled by a single switch located inside fire command room in ground floor as per latest fire norms, this switch should turn on the first light point of stair in GF and remaining staircase lights shall be considered in loop wiring. The staircase wiring shall be UPS powered for emergency backup)&lt;br&gt;One light point controlled by one way switch &lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.05 | 1.33 : Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. |  | 244 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.06 | 1.14.1 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required2x1.5 sq.mm + 1x1.5 sq.mm earth wire |  | 2145 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.07 | 1.14.2 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required2X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire |  | 1798 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.08 | 1.14.7 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire |  | 400 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.09 | 1.14.3 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required2 X 4 sq. mm + 1 X 4 sq. mm earth wire |  | 1300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.1 | 1.14.8 : Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required4 X 4 sq. mm + 2 X 4 sq. mm earth wire |  | 50 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.11 | 1.17.12 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 2.5 sq. mm |  | 222 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.12 | 1.17.21 : Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface / recessed steel/ PVC conduit as required.3 x 4 sq. mm |  | 134 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.13 | 1.21.1 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.20 mm |  | 80 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.14 | 1.21.2 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.25 mm |  | 220 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.15 | 1.21.3 : Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.32 mm |  | 260 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.16 | 1.40 : Providing and fixing plain 16/0.20 mm (0.50 sqmm) twin circular flexible FRLS PVC insulated, PVC sheathes copper cable direct on the wall with PVC clips etc as required. |  | 64 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.17 | 1.39 : Providing and fixing plain 16/0.20mm (0.50sqmm) twin flat flexible, FRLS PVC insulated, copper cable, in PVC sleeve of suitable size on the floor / wall, or side of the table / door etc. as required. |  | 7 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.18 | 1.43 : Providing and fixing extra conduit down rod of 20 mm dia, 2X10 cm length wiring with 2 X1.5 sq.mm FRLS PVC insulated, copper conductor, single core cable including painting etc. as required. (Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) |  | 384 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.19 | 1.49 : Numbering of ceiling fan / exhaust fan/ fluorescent fittings as required. |  | 353 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.2 | 1.26 : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. |  | 55 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.21 | 1.27.5 : Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.8 Module (125mmX125mm) |  | 34 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.22 | 1.28.2 : Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.3 Module |  | 44 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.23 | 1.28.5 : Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.8 Module |  | 19 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.24 | 1.24.1 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.5/6 amps switch |  | 40 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.25 | 1.24.3 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.15/16 amp switch |  | 57 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.26 | 1.24.4 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.3 pin 5/6 amp socket outlet |  | 199 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.27 | 1.24.5 : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.6 pin 15/16 amp socket outlet |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.28 | 1.31 : Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). |  | 68 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.29 | od16141/2023_2024 : Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 A &amp; 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required.&lt;br&gt; |  | 36 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.3 | 2.3.3 : Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCBIRCCB/Isolator12 way, Double door |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.31 | 2.4.1 : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface / recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)4 way (4 + 12), Double door |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.32 | 2.4.2 : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface / recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)6 way (4 + 18), Double door |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.33 | 2.4.3 : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface / recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)8 way (4 + 24), Double door |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.34 | 2.5.1 : Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required .(Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)4 way (4 + 12), Double door |  | 2 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.35 | 2.10.1 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Single pole |  | 110 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.36 | 2.10.3 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Double pole |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.37 | 2.10.4 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Triple pole |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.38 | 2.10.5 : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.Triple pole and neutral |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.39 | 2.11 : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. |  | 25 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.4 | 2.13.1 : Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.40 amps |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.41 | 2.14.1 : Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.25 amps |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.42 | od16206/2023_2024 : &quot;Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB),&lt;br&gt;having a sensitivity current 100 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.&quot;&lt;br&gt;40A&lt;br&gt;&lt;br&gt; |  | 7 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.43 | od16235/2023_2024 : Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker with overload protection (RCBO), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.&lt;br&gt;16A&lt;br&gt; |  | 3 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.44 | 2.25 : Supplying and fixing Cable End Box (Loose Wire Box) (IP 43) suitable for tripple pole and neutral, sheet steel, Vertical MCB distribution board, 415 V, on surface/ recess, complete with testing and commissioning etc. as required. |  | 8 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.45 | od16276/2023_2024 : &quot;Supply and fixing of SDF isolators in Sheet enclosures of following ratings, 415, with provision for cable glanding of cables as per schematic layout with Terminal Shrouds on both sides and Phase Barriers included. The enclosure should be of Sheet Steel constuction powder coated, spacious design for easy cable glanding and connection to terminals,conforming to IEC 60947-3, IS/IEC 60947-3, suitable for Cylindrical/DIN fuse-link inclusive of fuse links with Door interlock &amp; padlock facility, including spreader links, handle and all accesoires including mounting on wall and making clear all damages complete with testing and commissioning etc. as required.&lt;br&gt;&quot;&lt;br&gt;32A FP Isolator with enclosure&lt;br&gt; |  | 14 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.46 | od16471/2023_2024 : Supply, fixing, testing and commisioning of following rating, breaking capacity and pole, MCCB in existing Vertical Distribution Board with spredear links, terminal connections and all accesories as required making all necessary connections etc as required and instructed by engineer in charge/consultant complete with testing and commissioning etc. as required..&lt;br&gt;63 / 80 / 100 Amp (16-18)kA FP MCCB &lt;br&gt; |  | 4 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.47 | od16591/2023_2024 : Supply, installation, testing and commisioning of pluggable type surge arrester in suitable enclosure Class B+C/ Type 1+2 as per IEC 61643 -11 for lightning current equipotential bonding. Modular connectable arrestor with dynamic cut-off unit and visual status display for each cartridge. Nominal voltage -230V 50Hz, type single MOV with built in thermal fuse and cooling gel(L to N) &amp; spark gap encapsulated / non exhausting (N to E) . Total Lightning Impulse Current shall be as per IS standards (10/350&micro; sec) for Line to Neutral &amp; (10/350&micro; sec) for Neutral to Earth, Total Nominal discharge current- shall also be as per IS standards for Line to Neutral &amp; (8/20&micro; sec) for Neutral to Earth, Total Max discharge current &amp; voltage protection level - should be minmum as per IS standards (8/20&micro; sec). Response time &lt;25 nano sec (L to N), &lt; 100 nano sec (N to E). The arrestor shall be DIN rail mounting type etc complete with back up fuse as required and as per manaufacturer standard with enclosure for mounting the SPD near the DB, including copper cables for connection between SPD and DB incomer such that the cable length should be within 0.5m, including all accesories complete as required, testing and commisioning making good the damages&lt;br&gt; |  | 11 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
9.48 | od16835/2023_2024 : Supply, installation, testing and commisioning of pluggable type surge arrester in suitable enclosure Class B+C/ Type 1+2 as per IEC 61643 -11 for lightning current equipotential bonding. Modular connectable arrestor with dynamic cut-off unit and visual status display for each cartridge. It should be included Locking mechanism with vibration protection and voltage keying for safe operation of the device. Nominal voltage -230V 50Hz, type single MOV with built in thermal fuse and cooling gel(L to N) &amp; spark gap encapsulated / non exhausting (N to E) . Lightning Impulse Current - (10/350&micro; sec) for Line to Neutral &amp; (10/350&micro; sec) for Neutral to Earth, Nominal discharge current- (8/20&micro; sec) for Line to Neutral &amp; (8/20&micro; sec) for Neutral to Earth, Total Max discharge current - (8/20&micro; sec), Voltage protection level (L to N) &amp; (N to E), Operating temp -40&ordm; to +80&ordm;C should be as minimum as per IS standards with response time &lt;25 nano sec (L to N), &lt; 100 nano sec (N to E) DIN rail mounting type etc The arrestor shall be DIN rail mounting type etc complete with back up fuse as required and as per manaufacturer standard with enclosure for mounting the SPD near the DB, including copper cables for connection between SPD and DB incomer such that the cable length should be within 0.5m, including all accesories complete as required, testing and commisioning making good the damages&lt;br&gt; |  | 3 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10 | EARTHING PROTECTION | BI01010001010000000000000515BI01000011110 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.01 | 5.6 : Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. |  | 4 | set |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.02 | od15865/2023_2024 : Supply and laying the following sizes of Cu strips laid 0.6 m below ground level including excavating trench of suitable size and refilling ,including necessary clamps and bolts etc and all accessories as required for complete installation as instructed by engineer in charge/consultant. &lt;br&gt;25x3 mm Cu strip tinned at the point of contact&lt;br&gt; |  | 100 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.03 | od15866/2023_2024 : Supply and laying the following sizes of strips on cable tray/wall surface, including necessary clamps (each clamp not exceeding 60 cm) and bolts etc as required for complete installation as instructed by engineer in charge/consultant. &lt;br&gt;25x3mm Cu strips tinned at the point of contact&lt;br&gt; |  | 112 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.04 | od15867/2023_2024 : Supply and laying the following sizes of strips on cable tray/wall surface, including necessary clamps (each clamp not exceeding 60 cm) and bolts etc as required for complete installation as instructed by engineer in charge/consultant. &lt;br&gt;Copper wire No.10 SWG &lt;br&gt; |  | 80 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.05 | od15868/2023_2024 : Supply and laying the following sizes of strips on cable tray/wall surface, including necessary clamps (each clamp not exceeding 60 cm) and bolts etc as required for complete installation as instructed by engineer in charge/consultant. &lt;br&gt;Copper wire No.8 SWG &lt;br&gt; |  | 200 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.06 | od15871/2023_2024 : Supply and laying, including providing terminations for following PVC sheathed, unarmoured flexible copper conductor cable confirming to IS 7098 (part 1) ammended upto date for providing dedicated earthing. &lt;br&gt;1Cx6sq.mm Copper Flexible Cable (2XY) &lt;br&gt; |  | 300 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
10.07 | 5.20 : Providing and fixing earth bus of 50 mm X 5 mm copper strip on surface for connections etc. as required. |  | 1 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11 | MISCELLANEOUS ITEMS | BI01010001010000000000000515BI01000011111 | [6 empty] | 1
11.01 | od15872/2023_2024 : CABLE TRAYS&lt;br&gt;&quot;Supply and fixing of strip galvanised Perforated Cable tray confirming to IEC-61537 with galvanized 8mm threaded support system with 2 nos of anchor bolts with threaded rods from ceiling with cross channels of maximum width as per tray size bolted to it for supporting perforated cable tray and other accessories as required. The Tray shall be galvanized for corrosion protection confirming to DIN EN 10346 / ISO 1461 .The trays should be tested for a max. safe working load of 150 Kgs with a span distance of 1.5 meters and the deflection should be within the limits as per standardand and safety factor as per IEC &amp; ISO standards.Cable tray routing shop drawing shall got approved from Consultant before execution at site. Supports shall be placed at intervals as per loading of the tray but minimum interval of 100cm to be kept between the supports . Fabrication works by welding, cutting, bendng etc required for reducing of shape, size, providing bends and cross connections or offseting of cable trays as per site requirement shall also be considered in this scope without any additional cost in a proffesional manner. The cut areas shall be repainted with anticorrosive material to avoid rusting. All other assecories as required for complete installations shall be considered in this scope of work&lt;br&gt;&quot;&lt;br&gt;100mm width x 60mm Height&lt;br&gt; |  | 70 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.02 | od15873/2023_2024 : CABLE TRAYS&lt;br&gt;&quot;Supply and fixing of Cable Ladder trays confirming to IEC-61537.The Cable Ladder shall be made of 1.5mm thick sheet steel including supply and providing galvanized 8mm (200 - 300mm wide trays) &amp; 10mm (400-600mm wide trays) threaded support system with 2 nos of dropp in anchor bolts from ceiling with heavy duty profile rail of suitable size as per tray width.The cable Ladder shall be galvanized for corrosion protection confirming to ISO 1461 .The cable ladder should be tested for safe working load of 225 Kg/ Mtr (for 400 - 600mm wide tray) &amp; 140 Kg / Mtr (for 200 - 300mm wide tray) with a span distance of 2 Mtr the deflection should be within the limits as per standard. The cable ladder shall be supplied in standard length of 3000 mm. The rung size shall be of 30x15mmm size suitable for fixing the cable clamps, the space between the rungs shall be 300mm. Cable tray routing shop drawing shall got approved from Consultant before execution at site. Supports shall be placed at intervals as per loading of the tray but minimum interval of 60cm to be kept between the supports . Fabrication works by welding, cutting, bendng etc required for reducing of shape, size, providing bends and cross connections or offseting of cable trays as per site requirement shall also be considered in this scope without any additional cost in a proffesional manner. The cut areas shall be repainted with anticorrosive material to avoid rusting. All other assecories as required for complete installations shall be considered in this scope of work. Cable tray suspenders shall be the same make as the tray manufacturer including Wall and support brackets With flange-welded head plate Steel St Length 610mm suitable for 600mm ladder, Suspended support from ceiling With flange-welded head plate Steel St 50x50x400 for 450mm tray and &lt;br&gt;galvanized 8mm threaded support system with 2 nos of dropp in anchor bolts, with heavy duty profile rail for remaining cable tray sizes&quot;&lt;br&gt;600mm width x 75mm Height&lt;br&gt; |  | 25 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.03 | 2.21 : Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.04 | od15874/2023_2024 : Supply and fixing of 4 Kg ABC Dry Powder (Stored Pressure) Type Fire Extinguisher. pressurized with dry nitrogen gas at 15 bar. Design, construction and testing as per IS 2171-1999 external epoxy powder coating with PO Red Shade No. 538 of IS 5, Supplied with standard accessories.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.05 | od15875/2023_2024 : Supply and providing First Aid Box.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.06 | od15876/2023_2024 : Supply and providing laminated First Aid chart duly framed and placed in a conspicuous location for clear vision.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.07 | od15878/2023_2024 : Supply &amp; fixing Laminated drawings of electrical lay out, schematic drawing etc on good frame work.&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.08 | od15879/2023_2024 : Supply and providing MS chequered plate of suitable thickness including cutting, welding, painting etc. as required for cable duct covering etc.&lt;br&gt; |  | 1 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.09 | od15880/2023_2024 : Supply &amp; fixing of Class A Electrical rubber mat, used for up to 11 kV, Dielectric Strength of 33 kV , as per IS. 15652 - 2006 in front of various type HT equipments with ISI certification mark of standard 1 Mtr width.The work includes cleaning of the floor, fixing of insulation mat by using suitable adhesive, waterproofing compound, sealing materials etc., complete as required &lt;br&gt; |  | 8 | sqm |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
11.1 | 14.15.3 : Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required.120 mm dia (OD-120 mm & ID-103 mm nominal) |  | 40 | metre |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12 | CIVIL ITEMS | BI01010001010000000000000515BI01000011112 | [6 empty] | 1
12.01 | 10.2 : Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. |  | 64 | kg |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
12.02 | 10.18 : Providing and fixing circular / hexagonal cast iron or M.S. sheet box for ceiling fan clamp, of internal dia 140 mm, 73 mm height, top lid of 1.5 mm thick M.S. sheet with its top surface hacked for proper bonding, top lid shall be screwed into the cast iron/M.S. sheet box by means of 3.3 mm dia round headed screws, one lock at the corners. Clamp shall be made of 12 mm dia M.S. bar bent to shape as per standard drawing . |  | 350 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
13 | MV PANELS | BI01010001010000000000000515BI01000011113 | [6 empty] | 1 | [45 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13.01 | od16325/2023_2024 : CPRI CERTIFIED MV PANELS AS PER IS 8623Fabrication, supply, erection, testing and commissioning of dust and vermin proof, floor / wall mounted, front operated MV panel board as per IS 8623, CPRI Certified, compartmentalised (minimum form 3b) complete with hinged and earthed front doors with name plate, danger notice board, heavy duty rubber gaskets, removable gland plates made out of 3mm thick sheet steel including all components as shown in the schematic drawing. All opening parts of the panel shall be sealable. These panel should include surge arrester Class B or Class B+C/ Class 1+2 as per IEC 61643 (IP 20) with remote indication for defective arresters, arrester Spark Gap type to connect between Neutral and Earth.complete with back up fuse for SPD protection as per manufacturer standard. Providing all connections and interconnections as required and providing all accessories as required for complete installation as instructed by engineer in charge/consultant and as shown in the schematic layout provided. All switchgears shall be with with spreader links and rotary handle. Providing all connections and interconnections as required and providing all accessories as required for complete installation as instructed by engineer in charge/consultant and as shown in the schematic layout provided. Necessary electrical and mechanical interlocking arrangements shall be provided as per scehmatic drawing to achieve operational functionality.All panels shall be with separate channels isolated from LT cable chambers for running of RS485 &amp; other ELV cables for integration with EMS &amp; IBMS. Switchgears and meters shall be with necessary communication ports for integration with BMS &amp; EMS and Potential free contacts for BMS. All panel meters should be with RS485 ports for EMS integration. All Multifunction meter shall be as per IEC 62053-21, class 1, having multiline LED display with following parameters -Phase wise instantaneous and Average values &ndash; Voltage, Current, Power Factor, Phase wise instantaneous and Average values &ndash; Active Power, Reactive Power lead &amp; lag, Apparent Power, Import &amp; Export Cumulative values&ndash; Active Energy, Reactive Energy lead &amp; lag, Apparent Energy, 4. PF for 3 phases and average,Instantaneous Frequency,Total Harmonics Distortion &ndash; Phase wise Voltage and Phase wise Current, Min and max of VLL, VLN, A, F, W, VA, VAr, PF with date and time stamp,Battery backed RTC with 2 years of power down time, Demand calculations based on W, VA, VAr, 10. Demand sync &ndash; Sliding window or block window site selectable, Demand interval: 5 to 30 min, Individual harmonics upto 15th order for voltage and current, Percentage Unbalance &ndash; Voltage and Current, Cumulative Run Hours, Sampling rate of 64 samples / cycle, Measuring circuit burden should be lesser than 0.2 VA, Aux burden &lt; 5VA, Meter shall be suitable for CT secondary 1A /5A including CTs, site programmable CT &amp; PT ratio, Meters shall have RS485 port with MODBUS RTU protocol, with IP 51 protection from front end preventing dust and moisture entry, meters shall be capable of integration with EMS Software.All opening parts of the panel shall be sealable. Panels shall be complete with Al bus bars, separate earth bus bar to be provided through out the length of the panel along with base chanel of suitable size, cable alleys as per requirement, complete, numbering, danger plate etc as required as per specifications and drawings. Current density for busbarsize shall be designed considering not more than 0.8 A/sq.mm for aluminium. The switchgear live parts shall be isolated with proper insulation material. All switchgears shall be with spreader links, operating knobs/handles, DIN rail provision for isolators with required cable alleys. The panel design shall be in accordance with IS &amp; Kerala state norms. All panels shall be cable alleys and seperate bus bar compartments for easy terminations as per KSEI standards with proper clearances. Incomer -EB Incomer - 250A 36kA FP Microprocessor based MCCB having isolation duty &amp; 3 O/C &amp;1 E/F release with standby low set E/F relay - 1No.DG Incomer - 200A 36 kA FP MCCB Microprocessor based- 1 No.150A 433V best conductivity extensible p=n=25x6 Al TPN bus bar with SMC supports, heat shrinkable sleeves etc complete as required, as per IEC norms.RYB phase indicating LED lamps with control fuses and switches - 2 set.Multifunction meter as per IEC 62053-21, specified above including CTs and all accesories- 2 set.All CTs as required for complete installation.Class B Surge arrestor with HRC fuses for backup as per manufacturer standard, including copper cable connection between arrestor and fuses - 2 set.320A FP ATS with AMF 33B utilization category Outgoings-63A 25kA TP Thermal magnetic based MCCB - 1 nos.100A 25kA TP Thermal magnetic based MCCB - 2 no.63A 25kA TP Thermal magnetic based MCCB - 1 no .Multifunction meter as per IEC 62053-21, specified above including CTs and all accessories - 4 set.&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13.02 | od16487/2023_2024 : COMMON SERVICE PANEL -Income 63 TPN Isolator - 3 No.40A FP Isolator - 1 No.63A 433V, 25kA best conductivity extensible Al TPN bus bar with SMC supports, heat shrinkable sleeves etc complete as required. Necessary interlocking arrangement.75A 433V, 25kA best conductivity extensible P=N=25X3sq.mmAl TPN bus bar with SMC supports, heat shrinkable sleeves etc complete as required. RYB phase indicating LED lamps with control fuses and switches - 2 set.Surge Protection Device Class B+C/ Class 1+2 with HRC fuses for backup as per manufacturer standard, including copper cable connection between arrestor and fuses - 1 set.Multifunction meter as per IEC 62053-21, specified above including CTs and all accessories - 1 set.Surge Protection Device Class B with HRC fuses for backup as per manufacturer standard, including copper cable connection between arrestor and fuses - 1 set.Outgoings-63A TP ISOLATOR for 13HP pump along with starter w/o OLR, controllers, PB, indicators and all other accessories required as per fire norms - 1 nos.63A TP ISOLATOR - 2 nos.63A 25kA TP Thermal Magnetic Based MCCB - 4 nos.Multifunction meter as per IEC 62053-21, specified above including CTs and all accessories - 4 set.&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;&lt;br&gt;r -&lt;br&gt;&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13.03 | od16823/2023_2024 : LT METERING CUBICLE (OUTDOOR)&lt;br&gt;Supply,installation testing and commisioning of cubicle type, dust and vermin proof, wall mounted cubicle suitable for out door operation enclosure made out of 16 SWG thick CRCA sheet, duly rust inhibited,degreasing,zinc phosphating and powder coated of approved colour and quality over a coat of zinc-cromatic primer, complete with hinged and earthed front doors including all connections and inter-connections as required as per the direction of engineer in charge, including following switchgear. &lt;br&gt;RYB phase indicating LED lamps - 1 set.&lt;br&gt;250A COF - 1Set&lt;br&gt;250A SFU - 1SET&lt;br&gt;LT TOD Meter with all interconnections, N.L and all accessories -1 No&lt;br&gt; |  | 1 | each |  |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information